Troubleshooting Profibus

If no communications is being experienced between a Profibus Master and a FieldServer Profibus Slave, check for the following most common issues:

- The baud rate for this driver must be specified in the configuration

- Check that the baud rate is specified in the Connections section of the configuration.

- Baud rate must match the baud rate being used on the network.

- The Node_ID must match the System_Station_Address in the configuration

- Having these two parameters match in the configuration tells the FieldServer that the buffer referenced in the Node_ID refers to the buffers in the Profibus card attached to the FieldServer.

- The gse file must match the FieldServer hardware being used

- FieldServer offers several hardware platforms that support Profibus. Each hardware platform requires it’s own gse file. Make sure that the gse file being used is the correct file for the hardware platform in use.

- The gse file can be opened with a text editor. The Vendor and model name can be checked in this file. For the FieldServer X40 Profibus MultiSlave, the Vendor is “SST”, and the Model Name is “5136-PBMS”. The current revision is 1.3, which uses Hardware revision 1.0 and software release 1.0

- The byte count for the gse profile must match the byte count configured in the FieldServer

- The gse being used is either going to allow the client to select the bytes (via the network configuration tool) to be used, or the byte make-up will be fixed and specified in the gse. Either way, the largest byte offset used by the client must match the largest byte offset configured in the FieldServer.

- When selecting byte count with a network configuration tool, the total amount of bytes/words/bits setup per Input/Output buffer in the FieldServer configuration map descriptors must match those selected in the network config tool otherwise a connection length mismatch will occur and the connection will not be established. The Fieldserver shows the connection size it expects on the F (driver message) screen in the RUI utility in order that this value may be checked against the network configuration tool.

- The FieldServer may have bridge.bss loaded, which will configure it as a master

- The bridge.bss file is loaded by default when FieldServers ship with the default Profibus Master configuration. This file must not exist in applications where FieldServer is being used as a slave.

- To check for the file, try uploading the file from the FieldServer using the RUI Utility. If it uploads successfully, then it will need to be deleted. See the FieldServer Utilities manual for instructions on how to do this.

- The FieldServer may be missing the pfbdp.ss1 file

- This file is compulsory for all SST Profibus applications, and may be missing for some reason.

- To check for the file, try uploading the file from the FieldServer using the RUI Utility. If it uploads successfully, then this is not the problem.

- The direction of the communications (Input/Output Buffer) may be incorrectly configured.

- Buffer names can be confusing, especially when looking at the Slave. The buffers are named according to their direction of communication in the Master. Hence, an Input buffer in the slave will write data to the master, and data will be received from the master in the output buffer.

- Remember that as a slave, the FieldServer will have to write data into the input buffer (function=wrbc), and read data from the output buffer (function=rdbc).

- The Profibus card may be faulty.

- If this is the case, then there will be an error message in the FieldServer RUI error screen indicating that the card could not be reached. Check for this message. If it is there, try opening up the FieldServer and re-seating the card. If this does not help, contact FieldServer Technical support for jumper settings on the card, and further possible troubleshooting or return authorization.

- The Data Type/Offset/Length combination may be incorrectly set up

- In the FieldServer configuration, the Offset Parameter almost always refers to the buffer offset in bytes (starting at 0), regardless of data type. The only exception is the BIT data type which specifies offset in bits to allow for offsets that are not a multiple of 8. The Length parameter always refers to length in items, which means Float data will be the number of float values, Word data will be the number of words, etc.