## Points List
[5 empty] | 0xxxx | 4xxxx | 1xxxx | 3xxxx
[5 empty] | 1 | 40001 | 10001 | 30001 | Add this number to the Bacnet Object Number to get the Modbus Address
This cilumns used to make a list of supported services
[5 empty] | Bo | Ao | Bi | Ai | Bacnet Objecs and Instance Numbers |  | Used to make BACnet Objects | Used to make BACnet Objects | Used to make BACnet Objects | Used to make BACnet Objects
0x01 – SET FIELD CONTROLLER SYSTEM GLOBALS | [10 empty] | Do not edit | Do not edit | Do not edit | Do not edit | Do not edit | 0x01 – SET FIELD CONTROLLER SYSTEM GLOBALS
demo=h01.html
template=type1.html
Transmits to Field Controller(s), system global information. This information is typically applicable to all Field Controllers within the system. The new values become effective immediately. This command would normally use the 'All Call' Field Controller address of 1940H, but may also be sent to an individual Field Controller
The payload of data is extracted from the Data Array as show below to form the message sent to the Controller
Map_Descriptors
| Data Array | Payload | [11 empty] | Map_Descriptor_Name , Data_Array_Name , Data_Array_Offset ,Data_Type , Object_ID , Function , Node_Name , Property ,Units , Data_Array_Low_Scale , Data_Array_High_Scale , Node_Low_Scale , Node_High_Scale ,Description,
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x01 | 0 |  | Trigger_SetFieldGlobals |  | 0 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 0 | 0x01_Trigger_SetFieldGlobals , DA_Bv ,000 ,Bv ,000 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x01 | 1 | 1 | UnixTime | UINT32 |  | 0 |  |  |  | Unsigned value represneting the current Unix Time | 000 | Av | 0 | 0x01_UnixTime , DA_Av ,000 ,Av ,000 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value represneting the current ,
0x01 | 2 | 2 | DSTEnable | Byte |  | 1 |  |  |  | Value indicating whether or not DST is enabled in the controller. Range is 0 to 1. 0 = DST not enabled- 1 = DST enabled | 000 | Av | 1 | 0x01_DSTEnable , DA_Av ,001 ,Av ,001 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not DST is ,
0x01 | 3 | 3 | DSTTime | UINT16 |  | 2 |  |  |  | Value indicating time in to start/edn DST in Minutes After Midnight. Range is 0 to 1439 | 000 | Av | 2 | 0x01_DSTTime , DA_Av ,002 ,Av ,002 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating time in to start/edn D ,
0x01 | 4 | 4 | DSTStartWeek | Byte |  | 3 |  |  |  | Value indicating the week number in the month to start DST. Range is 1 to 5. 1= First week- 2 = Second week- 3 = third week- 4 = forth week- 5 = last week. | 000 | Av | 3 | 0x01_DSTStartWeek , DA_Av ,003 ,Av ,003 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the week number in the ,
0x01 | 5 | 5 | DSTStartDow | Byte |  | 4 |  |  |  | Value indicating the Day of Week to start DST. Range is 0 to 6. 0 = Sun- 1 = Mon- 2 = Tues- 3 = Wed- 4 = Thu- 5 = Fri- 6 = Sat. | 000 | Av | 4 | 0x01_DSTStartDow , DA_Av ,004 ,Av ,004 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Day of Week to sta ,
0x01 | 6 | 6 | DSTStartMonth | Byte |  | 5 |  |  |  | Value indicating the month to start DST. Range is 0 to 11. 0 Jan- 1 = Feb- 2 = Mar- 3 = Apr- 4 = May- 5 = Jun- 6 = Jul- 7 = Aug- 8 = Sep- 9 = Oct- 10 = Nov- 11 = Dec. | 000 | Av | 5 | 0x01_DSTStartMonth , DA_Av ,005 ,Av ,005 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the month to start DST ,
0x01 | 7 | 7 | DSTEndWeek | Byte |  | 6 |  |  |  | Value indicating the week number in the month to end DST.Range is 1 to 5. 1= First week- 2 = Second week- 3 = third week- 4 = forth week- 5 = last week | 000 | Av | 6 | 0x01_DSTEndWeek , DA_Av ,006 ,Av ,006 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the week number in the ,
0x01 | 8 | 8 | DSTEndDOW | Byte |  | 7 |  |  |  | Value indicating the Day of Week to end DST. Range is 0 to 6. 0 = Sun- 1 = Mon- 2 = Tues- 3 = Wed- 4 = Thu- 5 = Fri- 6 = Sat. | 000 | Av | 7 | 0x01_DSTEndDOW , DA_Av ,007 ,Av ,007 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Day of Week to end ,
0x01 | 9 | 9 | DSTEndMonth | Byte |  | 8 |  |  |  | Value indicating the month to end DST.Range is 1 to 5. 1= First month- 2 = Second month- 3 = third month- 4 = forth month- 5 = last month | 000 | Av | 8 | 0x01_DSTEndMonth , DA_Av ,008 ,Av ,008 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the month to end DST.R ,
0x01 | 10 | 10 | Language | Byte |  | 9 |  |  |  | Enumeratred Language. Range is 0 to 5. 0 = English- 1 = Spanish- 2 = French- 3 = German- 4 = Portuguese- 5 = Italian- 6 = Turkish- 7 = Polish- 8 = Czech- 9 = Chinese- 10 = Russion- 11 = Arabic. | 000 | Av | 9 | 0x01_Language , DA_Av ,009 ,Av ,009 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enumeratred Language. Range is 0 to 5. ,
0x01 | 11 | 11 | TimeFormat | Byte |  | 10 |  |  |  | Value indicating the time format to be used in the controller. Range is 0 to 1. 0 = 12-hour mode- 1 = 24-hour mode. | 000 | Av | 10 | 0x01_TimeFormat , DA_Av ,010 ,Av ,010 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the time format to be ,
0x01 | 12 | 12 | DateFormat | Byte |  | 11 |  |  |  | Value indicating the date format to be used in the controller. Range is 0 to 1. 0 = MM/DD/YYYY- 1 = DD/MM/YYYY. | 000 | Av | 11 | 0x01_DateFormat , DA_Av ,011 ,Av ,011 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the date format to be ,
0x01 | 13 | 13 | Units | Byte |  | 12 |  |  |  | Value indicating the measurements units to be used by the controller. Range is 0 to 1. 0 = English- 1 = Metric. | 000 | Av | 12 | 0x01_Units , DA_Av ,012 ,Av ,012 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the measurements units ,
0x01 | 14 | 14 | ReportLevel | Byte |  | 13 |  |  |  | Report Level for reporting controller activity. Range is 0 to 2. 0 = None - Controller will not initiate communications. 1 = Partial - Controller initiates alarm activity reporting communication. 2 = Full - Controller initiates station and alarm activity reporting communications. | 000 | Av | 13 | 0x01_ReportLevel , DA_Av ,013 ,Av ,013 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Report Level for reporting controller a ,
0x01 | 15 | 15 | ReportInterval | Byte |  | 14 |  |  |  | Set Interval in seconds that the controller will report a change in the active station list (Command 72H). Range is 1 to 120. | 000 | Av | 14 | 0x01_ReportInterval , DA_Av ,014 ,Av ,014 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Set Interval in seconds that the contro ,
000
0x02 – REPORT FIELD CONTROLLER GLOBALS | [10 empty] | 000 |  |  |  |  | 0x02 – REPORT FIELD CONTROLLER GLOBALS
| demo=h01.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
| Transmits to the central current global values contained in the specific field controller. TOD (Time of Day) reports time (hr/min/sec) in 24-hour format. DC (Day Change) reports time (hr) in 24 hour format. Day of Schedule is a value pointer referring to an FCP. Length is a value specifying the schedule length referring to an FCP. | [9 empty] | 000
| When a response is received the payload of data is extracted and stored as shown below | [9 empty] | 000
000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x02 | 0 | 1 | FwVers | UINT16 |  |  |  | 0 |  | Integer value of firmware version times 100. | 000 | Ai | 0 | 0x02_FwVers , DA_Ai ,000 ,Ai ,000 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Integer value of firmware version times ,
0x02 | 1 | 2 | EngRev | Byte |  |  |  | 1 |  | Integer value of firmware Engineering Revision. | 000 | Ai | 1 | 0x02_EngRev , DA_Ai ,001 ,Ai ,001 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Integer value of firmware Engineering R ,
0x02 | 2 | 3 | Size | UINT16 |  |  |  | 2 |  | Number of stations detected in the controller. For conventional controllers- ranse is 6 to 54 in 6 station increments. For decoder controllers- range is 75 to 225 in 75 station increments. A value of 0 is also valid for either controller type and indicates that no stations were detected. | 000 | Ai | 2 | 0x02_Size , DA_Ai ,002 ,Ai ,002 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Number of stations detected in the cont ,
0x02 | 3 | 4 | UnixTime | UINT32 |  |  |  | 3 |  | Unsigned value representing the current Unix Time. | 000 | Ai | 3 | 0x02_UnixTime , DA_Ai ,003 ,Ai ,003 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the current ,
0x02 | 4 | 5 | DSTEnable | Byte |  |  |  | 4 |  | Value indicating whether or not DST is enable in the controller. Range is 0 to 1. 0 = DST not enabled- 1 = DST enabled. | 000 | Ai | 4 | 0x02_DSTEnable , DA_Ai ,004 ,Ai ,004 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not DST is ,
0x02 | 5 | 6 | DSTTime | UINT16 |  |  |  | 5 |  | Value indicating the time in to start/end DST in Minutes After Midnight. Range is 0 to 1439. | 000 | Ai | 5 | 0x02_DSTTime , DA_Ai ,005 ,Ai ,005 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the time in to start/e ,
0x02 | 6 | 7 | DSTStartWeek | Byte |  |  |  | 6 |  | Value indicating the week number in the month to start DST. Range is 1 to 5. 1= First month- 2 = Second month- 3 = third month- 4 = forth month- 5 = last month | 000 | Ai | 6 | 0x02_DSTStartWeek , DA_Ai ,006 ,Ai ,006 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the week number in the ,
0x02 | 7 | 8 | DSTStartDOW | Byte |  |  |  | 7 |  | Value indicating the Day of Week to start DST. Range is 0 to 6. 0 = Sun- 1 = Mon- 2 = Tues- 3 = Wed- 4 = Thu- 5 = Fri- 6 = Sat. | 000 | Ai | 7 | 0x02_DSTStartDOW , DA_Ai ,007 ,Ai ,007 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Day of Week to sta ,
0x02 | 8 | 9 | DSTStartMonth | Byte |  |  |  | 8 |  | Value indicating the month to start DST. Range is 0 to 11. 0 Jan- 1 = Feb- 2 = Mar- 3 = Apr- 4 = May- 5 = Jun- 6 = Jul- 7 = Aug- 8 = Sep- 9 = Oct- 10 = Nov- 11 = Dec. | 000 | Ai | 8 | 0x02_DSTStartMonth , DA_Ai ,008 ,Ai ,008 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the month to start DST ,
0x02 | 9 | 10 | DSTEndWeek | Byte |  |  |  | 9 |  | Value indicating the week number in the month to end DST.Range is 1 to 5. 1= First week- 2 = Second week- 3 = third week- 4 = forth week- 5 = last week | 000 | Ai | 9 | 0x02_DSTEndWeek , DA_Ai ,009 ,Ai ,009 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the week number in the ,
0x02 | 10 | 11 | DSTEndDOW | Byte |  |  |  | 10 |  | Value indicating the Day of Week to end DST. Range is 0 to 6. 0 = Sun- 1 = Mon- 2 = Tues- 3 = Wed- 4 = Thu- 5 = Fri- 6 = Sat. | 000 | Ai | 10 | 0x02_DSTEndDOW , DA_Ai ,010 ,Ai ,010 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Day of Week to end ,
0x02 | 11 | 12 | DSTEndMonth | Byte |  |  |  | 11 |  | Value indicating the month to end DST.Range is 1 to 5. 1= First month- 2 = Second month- 3 = third month- 4 = forth month- 5 = last month | 000 | Ai | 11 | 0x02_DSTEndMonth , DA_Ai ,011 ,Ai ,011 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the month to end DST.R ,
0x02 | 12 | 13 | Language | Byte |  |  |  | 12 |  | Enumeratred Language. Range is 0 to 5. 0 = English- 1 = Spanish- 2 = French- 3 = German- 4 = Portuguese- 5 = Italian- 6 = Turkish- 7 = Polish- 8 = Czech- 9 = Chinese- 10 = Russion- 11 = Arabic. | 000 | Ai | 12 | 0x02_Language , DA_Ai ,012 ,Ai ,012 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enumeratred Language. Range is 0 to 5. ,
0x02 | 13 | 14 | TimeFormat | Byte |  |  |  | 13 |  | Value indicating the time format to be used in the controller. Range is 0 to 1. 0 = 12-hour mode- 1 = 24-hour mode. | 000 | Ai | 13 | 0x02_TimeFormat , DA_Ai ,013 ,Ai ,013 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the time format to be ,
0x02 | 14 | 15 | DateFormat | Byte |  |  |  | 14 |  | Value indicating the date format to be used in the controller. Range is 0 to 1. 0 = MM/DD/YYYY- 1 = DD/MM/YYYY. | 000 | Ai | 14 | 0x02_DateFormat , DA_Ai ,014 ,Ai ,014 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the date format to be ,
0x02 | 15 | 16 | Units | Byte |  |  |  | 15 |  | Value indicating the measurement units to be used by the controller. Rnage is 0 to 1. 0 = English- 1 = Metric. | 000 | Ai | 15 | 0x02_Units , DA_Ai ,015 ,Ai ,015 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the measurement units ,
0x02 | 16 | 17 | ReportLevel | Byte |  |  |  | 16 |  | Report Level for reporting controller activity. Range is 0 to 2. 0 = None - Controller will not initiate communications. 1= Partial - Controller initiates alarm activity reporting communications. 2 = Full - Controller initiates tation and alarm activity reporting communications. | 000 | Ai | 16 | 0x02_ReportLevel , DA_Ai ,016 ,Ai ,016 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Report Level for reporting controller a ,
0x02 | 17 | 18 | ReportInterval | Byte |  |  |  | 17 |  | Sets Interval in second that the controller will report a change in the active station list (command 72H). Range is 1 to 120. | 000 | Ai | 17 | 0x02_ReportInterval , DA_Ai ,017 ,Ai ,017 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sets Interval in second that the contro ,
0x02 | 18 | 19 | OffStatus | Byte |  |  |  | 18 |  | Value indicating off status of controller: 0 = Controller is NOT OFF (Running). 1 = Controller is OFF (Rain Shutdown or Programmable off) | 000 | Ai | 18 | 0x02_OffStatus , DA_Ai ,018 ,Ai ,018 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating off status of controll ,
0x02 | 19 | 20 | OffDays | Byte |  |  |  | 19 |  | Value indicating the nuber of off days set in the controller. This value is only valid if OffStatus byte indicates controller is off. Range is 0 to 180. 0 = Rain Shutdown (Indefinite). 1 to 180 = Programmable Shutdown days. | 000 | Ai | 19 | 0x02_OffDays , DA_Ai ,019 ,Ai ,019 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the nuber of off days ,
000
0x03 – SET STACKING MODE AND LIMITS | [10 empty] | 000 |  |  |  |  | 0x03 – SET STACKING MODE AND LIMITS
| demo=h03.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
| This command sends the Stacking Mode and Limits to be used by the Controller for irrigation. | [9 empty] | 000
000
| The payload of data is extracted from the Data Array as show below to form the message sent to the Controller | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x03 | 0 | 1 | Trigger_SetStackingMode |  | 1 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 1 | 0x03_Trigger_SetStackingMode , DA_Bv ,001 ,Bv ,001 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x03 | 1 | 2 | StackMode | Byte |  | 15 |  |  |  | Contains the Stacking Mode to be used by the Controller. Range is 0 to 1. 0 = Stack/Ovelap- 1 = Smartstack | 000 | Av | 15 | 0x03_StackMode , DA_Av ,015 ,Av ,015 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the Stacking Mode to be used b ,
0x03 | 2 | 3 | SmartStackLimit | Byte |  | 16 |  |  |  | Contains the SmartStack Program Limit when the Stack Mode is set to SmartStack. Ranse is 2 to 32. | 000 | Av | 16 | 0x03_SmartStackLimit , DA_Av ,016 ,Av ,016 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the SmartStack Program Limit w ,
0x03 | 3 | 4 | FcSimStaLimit | Byte |  | 17 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 17 | 0x03_FcSimStaLimit , DA_Av ,017 ,Av ,017 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 4 | 5 | Prg1SimStaLimit | Byte |  | 18 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 18 | 0x03_Prg1SimStaLimit , DA_Av ,018 ,Av ,018 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 5 | 6 | Prg2SimStaLimit | Byte |  | 19 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 19 | 0x03_Prg2SimStaLimit , DA_Av ,019 ,Av ,019 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 6 | 7 | Prg3SimStaLimit | Byte |  | 20 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 20 | 0x03_Prg3SimStaLimit , DA_Av ,020 ,Av ,020 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 7 | 8 | Prg4SimStaLimit | Byte |  | 21 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 21 | 0x03_Prg4SimStaLimit , DA_Av ,021 ,Av ,021 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 8 | 9 | Prg5SimStaLimit | Byte |  | 22 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 22 | 0x03_Prg5SimStaLimit , DA_Av ,022 ,Av ,022 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 9 | 10 | Prg6SimStaLimit | Byte |  | 23 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 23 | 0x03_Prg6SimStaLimit , DA_Av ,023 ,Av ,023 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 10 | 11 | Prg7SimStaLimit | Byte |  | 24 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 24 | 0x03_Prg7SimStaLimit , DA_Av ,024 ,Av ,024 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 11 | 12 | Prg8SimStaLimit | Byte |  | 25 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 25 | 0x03_Prg8SimStaLimit , DA_Av ,025 ,Av ,025 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 12 | 13 | Prg9SimStaLimit | Byte |  | 26 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 26 | 0x03_Prg9SimStaLimit , DA_Av ,026 ,Av ,026 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 13 | 14 | Prg10SimStaLimit | Byte |  | 27 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 27 | 0x03_Prg10SimStaLimit , DA_Av ,027 ,Av ,027 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 14 | 15 | Prg11SimStaLimit | Byte |  | 28 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 28 | 0x03_Prg11SimStaLimit , DA_Av ,028 ,Av ,028 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 15 | 16 | Prg12SimStaLimit | Byte |  | 29 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 29 | 0x03_Prg12SimStaLimit , DA_Av ,029 ,Av ,029 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 16 | 17 | Prg13SimStaLimit | Byte |  | 30 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 30 | 0x03_Prg13SimStaLimit , DA_Av ,030 ,Av ,030 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 17 | 18 | Prg14SimStaLimit | Byte |  | 31 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 31 | 0x03_Prg14SimStaLimit , DA_Av ,031 ,Av ,031 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 18 | 19 | Prg15SimStaLimit | Byte |  | 32 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 32 | 0x03_Prg15SimStaLimit , DA_Av ,032 ,Av ,032 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 19 | 20 | Prg16SimStaLimit | Byte |  | 33 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 33 | 0x03_Prg16SimStaLimit , DA_Av ,033 ,Av ,033 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 20 | 21 | Prg17SimStaLimit | Byte |  | 34 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 34 | 0x03_Prg17SimStaLimit , DA_Av ,034 ,Av ,034 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 21 | 22 | Prg18SimStaLimit | Byte |  | 35 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 35 | 0x03_Prg18SimStaLimit , DA_Av ,035 ,Av ,035 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 22 | 23 | Prg19SimStaLimit | Byte |  | 36 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 36 | 0x03_Prg19SimStaLimit , DA_Av ,036 ,Av ,036 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 23 | 24 | Prg20SimStaLimit | Byte |  | 37 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 37 | 0x03_Prg20SimStaLimit , DA_Av ,037 ,Av ,037 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 24 | 25 | Prg21SimStaLimit | Byte |  | 38 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 38 | 0x03_Prg21SimStaLimit , DA_Av ,038 ,Av ,038 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 25 | 26 | Prg22SimStaLimit | Byte |  | 39 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 39 | 0x03_Prg22SimStaLimit , DA_Av ,039 ,Av ,039 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 26 | 27 | Prg23SimStaLimit | Byte |  | 40 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 40 | 0x03_Prg23SimStaLimit , DA_Av ,040 ,Av ,040 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 27 | 28 | Prg24SimStaLimit | Byte |  | 41 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 41 | 0x03_Prg24SimStaLimit , DA_Av ,041 ,Av ,041 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 28 | 29 | Prg25SimStaLimit | Byte |  | 42 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 42 | 0x03_Prg25SimStaLimit , DA_Av ,042 ,Av ,042 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 29 | 30 | Prg26SimStaLimit | Byte |  | 43 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 43 | 0x03_Prg26SimStaLimit , DA_Av ,043 ,Av ,043 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 30 | 31 | Prg27SimStaLimit | Byte |  | 44 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 44 | 0x03_Prg27SimStaLimit , DA_Av ,044 ,Av ,044 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 31 | 32 | Prg28SimStaLimit | Byte |  | 45 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 45 | 0x03_Prg28SimStaLimit , DA_Av ,045 ,Av ,045 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 32 | 33 | Prg29SimStaLimit | Byte |  | 46 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 46 | 0x03_Prg29SimStaLimit , DA_Av ,046 ,Av ,046 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 33 | 34 | Prg30SimStaLimit | Byte |  | 47 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 47 | 0x03_Prg30SimStaLimit , DA_Av ,047 ,Av ,047 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 34 | 35 | Prg31SimStaLimit | Byte |  | 48 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 48 | 0x03_Prg31SimStaLimit , DA_Av ,048 ,Av ,048 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x03 | 35 | 36 | Prg32SimStaLimit | Byte |  | 49 |  |  |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Av | 49 | 0x03_Prg32SimStaLimit , DA_Av ,049 ,Av ,049 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
000
0x04 – REPORT STACKING MODE AND LIMITS | [10 empty] | 000 |  |  |  |  | 0x04 – REPORT STACKING MODE AND LIMITS
| demo=h03.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
| This command reports the Stacking Mode and Limits being used by the controller for irrigation. The Stack Mode, SmartStack Limit, and the FC Simultaneous Station Limit are always used by the controller to limit the number of simultaneous active Stations. The Program Simultaneous Station Limit is only used by the Controller if Flow Management is enabled and will be used to limit the number of simultaneous Stations that may be active within each Program. | [9 empty] | 000
| This command and the response do not carry a payload of data. | [9 empty] | 000
000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x04 | 0 | 1 | StackMode | Byte |  |  |  | 20 |  | Contains the Stacking Mode to be used by the Controller. Range is 0 to 1. 0 = Stack/Overlap- 1 = Smartstack. | 000 | Ai | 20 | 0x04_StackMode , DA_Ai ,020 ,Ai ,020 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the Stacking Mode to be used b ,
0x04 | 1 | 2 | SmartStackLimit | Byte |  |  |  | 21 |  | Contains the SmartStack Program Limit when the StackMode is set to SmartStack. Range is 2 to 32. | 000 | Ai | 21 | 0x04_SmartStackLimit , DA_Ai ,021 ,Ai ,021 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the SmartStack Program Limit w ,
0x04 | 2 | 3 | FcSimStaLimit | Byte |  |  |  | 22 |  | Contains the maximum number of Stations that can run simultaneously in the Controller. Range is 1 to 14 fo Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 22 | 0x04_FcSimStaLimit , DA_Ai ,022 ,Ai ,022 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 3 | 4 | Prg1SimStaLimit | Byte |  |  |  | 23 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 23 | 0x04_Prg1SimStaLimit , DA_Ai ,023 ,Ai ,023 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 4 | 5 | Prg2SimStaLimit | Byte |  |  |  | 24 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 24 | 0x04_Prg2SimStaLimit , DA_Ai ,024 ,Ai ,024 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 5 | 6 | Prg3SimStaLimit | Byte |  |  |  | 25 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 25 | 0x04_Prg3SimStaLimit , DA_Ai ,025 ,Ai ,025 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 6 | 7 | Prg4SimStaLimit | Byte |  |  |  | 26 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 26 | 0x04_Prg4SimStaLimit , DA_Ai ,026 ,Ai ,026 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 7 | 8 | Prg5SimStaLimit | Byte |  |  |  | 27 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 27 | 0x04_Prg5SimStaLimit , DA_Ai ,027 ,Ai ,027 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 8 | 9 | Prg6SimStaLimit | Byte |  |  |  | 28 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 28 | 0x04_Prg6SimStaLimit , DA_Ai ,028 ,Ai ,028 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 9 | 10 | Prg7SimStaLimit | Byte |  |  |  | 29 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 29 | 0x04_Prg7SimStaLimit , DA_Ai ,029 ,Ai ,029 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 10 | 11 | Prg8SimStaLimit | Byte |  |  |  | 30 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 30 | 0x04_Prg8SimStaLimit , DA_Ai ,030 ,Ai ,030 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 11 | 12 | Prg9SimStaLimit | Byte |  |  |  | 31 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 31 | 0x04_Prg9SimStaLimit , DA_Ai ,031 ,Ai ,031 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 12 | 13 | Prg10SimStaLimit | Byte |  |  |  | 32 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 32 | 0x04_Prg10SimStaLimit , DA_Ai ,032 ,Ai ,032 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 13 | 14 | Prg11SimStaLimit | Byte |  |  |  | 33 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 33 | 0x04_Prg11SimStaLimit , DA_Ai ,033 ,Ai ,033 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 14 | 15 | Prg12SimStaLimit | Byte |  |  |  | 34 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 34 | 0x04_Prg12SimStaLimit , DA_Ai ,034 ,Ai ,034 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 15 | 16 | Prg13SimStaLimit | Byte |  |  |  | 35 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 35 | 0x04_Prg13SimStaLimit , DA_Ai ,035 ,Ai ,035 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 16 | 17 | Prg14SimStaLimit | Byte |  |  |  | 36 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 36 | 0x04_Prg14SimStaLimit , DA_Ai ,036 ,Ai ,036 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 17 | 18 | Prg15SimStaLimit | Byte |  |  |  | 37 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 37 | 0x04_Prg15SimStaLimit , DA_Ai ,037 ,Ai ,037 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 18 | 19 | Prg16SimStaLimit | Byte |  |  |  | 38 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 38 | 0x04_Prg16SimStaLimit , DA_Ai ,038 ,Ai ,038 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 19 | 20 | Prg17SimStaLimit | Byte |  |  |  | 39 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 39 | 0x04_Prg17SimStaLimit , DA_Ai ,039 ,Ai ,039 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 20 | 21 | Prg18SimStaLimit | Byte |  |  |  | 40 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 40 | 0x04_Prg18SimStaLimit , DA_Ai ,040 ,Ai ,040 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 21 | 22 | Prg19SimStaLimit | Byte |  |  |  | 41 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 41 | 0x04_Prg19SimStaLimit , DA_Ai ,041 ,Ai ,041 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 22 | 23 | Prg20SimStaLimit | Byte |  |  |  | 42 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 42 | 0x04_Prg20SimStaLimit , DA_Ai ,042 ,Ai ,042 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 23 | 24 | Prg21SimStaLimit | Byte |  |  |  | 43 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 43 | 0x04_Prg21SimStaLimit , DA_Ai ,043 ,Ai ,043 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 24 | 25 | Prg22SimStaLimit | Byte |  |  |  | 44 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 44 | 0x04_Prg22SimStaLimit , DA_Ai ,044 ,Ai ,044 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 25 | 26 | Prg23SimStaLimit | Byte |  |  |  | 45 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 45 | 0x04_Prg23SimStaLimit , DA_Ai ,045 ,Ai ,045 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 26 | 27 | Prg24SimStaLimit | Byte |  |  |  | 46 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 46 | 0x04_Prg24SimStaLimit , DA_Ai ,046 ,Ai ,046 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 27 | 28 | Prg25SimStaLimit | Byte |  |  |  | 47 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 47 | 0x04_Prg25SimStaLimit , DA_Ai ,047 ,Ai ,047 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 28 | 29 | Prg26SimStaLimit | Byte |  |  |  | 48 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 48 | 0x04_Prg26SimStaLimit , DA_Ai ,048 ,Ai ,048 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 29 | 30 | Prg27SimStaLimit | Byte |  |  |  | 49 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 49 | 0x04_Prg27SimStaLimit , DA_Ai ,049 ,Ai ,049 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 30 | 31 | Prg28SimStaLimit | Byte |  |  |  | 50 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 50 | 0x04_Prg28SimStaLimit , DA_Ai ,050 ,Ai ,050 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 31 | 32 | Prg29SimStaLimit | Byte |  |  |  | 51 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 51 | 0x04_Prg29SimStaLimit , DA_Ai ,051 ,Ai ,051 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 32 | 33 | Prg30SimStaLimit | Byte |  |  |  | 52 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 52 | 0x04_Prg30SimStaLimit , DA_Ai ,052 ,Ai ,052 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 33 | 34 | Prg31SimStaLimit | Byte |  |  |  | 53 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 53 | 0x04_Prg31SimStaLimit , DA_Ai ,053 ,Ai ,053 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
0x04 | 34 | 35 | Prg32SimStaLimit | Byte |  |  |  | 54 |  | Contains the maximum number of Stations that can run simultaneously in Program X when running as a Flow Managed Program. One value is sent for each of the 32 Programs. Range is 1 to 14 for Conventional Controllers and 1 to 30 for Decoder Controllers. | 000 | Ai | 54 | 0x04_Prg32SimStaLimit , DA_Ai ,054 ,Ai ,054 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the maximum number of Stations ,
000
0x06 – Mute | [10 empty] | 000 |  |  |  |  | 0x06 – Mute
| demo=cmds.html | [9 empty] | 000
| Transmits to a field controller, a command that used to prevent the field controller from initiating any random communication directed to the central when the controller is in a response mode other than NONE. This mode can be cancelled by sending the reciprocal command (07H) or will be cancelled by the controller at day change. | [9 empty] | 000
| This command and the response do not carry a payload of data. | [9 empty] | 000
000
| Payload | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x06 | N/A Command does not carry data | [9 empty] | 000
0x06 | 0 |  | Trigger_Mute |  | 2 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 2 | 0x06_Trigger_Mute , DA_Bv ,002 ,Bv ,002 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
000
0x07 - Reset Mute | [10 empty] | 000 |  |  |  |  | 0x07 - Reset Mute
| demo=cmds.html | [9 empty] | 000
| Transmits to a field controller, a command that is the reciprocal command of Mute (06). It will reset the controller for random communications. This is the normal or default mode. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
000
| Payload | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x07 | N/A Command does not carry data | [9 empty] | 000
0x07 | 0 |  | Trigger_MuteReset |  | 3 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 3 | 0x07_Trigger_MuteReset , DA_Bv ,003 ,Bv ,003 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
000
0x0A – REPORT VERSIONS | [10 empty] | 000 |  |  |  |  | 0x0A – REPORT VERSIONS
| demo=h0a.html | [9 empty] | 000
| template=type2.html | [9 empty] | 000
| This command will report the currnt firmware version of the Face Pack and all installed modules in the controller. | [9 empty] | 000
| When a response is received the payload of data is extracted and stored as shown below | [9 empty] | 000
000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x0A | 0 | 1 | ModType | Byte |  |  |  | 55 | [55 , 'ModType '], | Value containing Module Type. Valid values are 1 to 19. 1 = Facepack- 2 = Power Supply- 3 = Decoder 75-station Module- 4 = Conventional 6-Station Module- 5 to 15 = N/A (Future)- 16 = Flow Module- 17 = Solar-Sync- 18 = WiFi Module- 19 = LAN Module | 000 | Ai | 55 | 0x0A_[55 , 'ModType '],ModType , DA_Ai ,055 ,Ai ,055 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing Module Type. Valid val ,
0x0A | 1 | 2 | Slot | Byte |  |  |  | 56 | [56 , 'Slot '], | Value indicating slot that module is installed into if applicable. Valid values are 0 to 9. A calue of 0 indicates that the slot number is not applicable. | 000 | Ai | 56 | 0x0A_[56 , 'Slot '],Slot , DA_Ai ,056 ,Ai ,056 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating slot that module is in ,
0x0A | 2 | 3 | ModFwVersion | UINT16 |  |  |  | 57 | [57 , 'ModFwVersion '], | For all modules unless noted below - Value is integer value of module firmware version times 100 (e.g. v1.01 = 101d). A value of 0 indicated that there is not a firmware version for this module. For the WiFi moduel- it is the hex value of the firmware version which should be displayed as a hex value- not decimal. For the Solar-Sync- contains a bit-mapped value with solar-sync firmware version and communications type. Bit 15: 0 = Wired Sensor- 1 = Wireless Sensor. Bit 14-0: Integer value of module firmware version times 100. | 000 | Ai | 57 | 0x0A_[57 , 'ModFwVersion '],ModFwVersion , DA_Ai ,057 ,Ai ,057 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,For all modules unless noted below - Va ,
0x0A | 3 | 4 | ModEngRevision | Byte |  |  |  | 58 | [58 , 'ModEngRevision '], | For all modules unless noted below - Value is integer value of firmware Engineering Revision (Range 0 to 255). This value is only applicable if the ModFwVersion value is not 0. For the WiFi Module and Solar-Sync- this value is not applicable. | 000 | Ai | 58 | 0x0A_[58 , 'ModEngRevision '],ModEngRevision , DA_Ai ,058 ,Ai ,058 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,For all modules unless noted below - Va ,
000
0x0C – SET FLOW OPERATION PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x0C – SET FLOW OPERATION PARAMETERS
| demo=h0c.html | [9 empty] | 000
| Template=1 | [9 empty] | 000
| This command enables or disables Flow Management and Flow Monitoring in the controller. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x0C | 0 |  | Trigger_SetFlowParams |  | 4 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 4 | 0x0C_Trigger_SetFlowParams , DA_Bv ,004 ,Bv ,004 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x0C | 1 | 1 | FlowMgrEnable | Byte |  | 50 |  |  |  | Value indicates whether or not to enable the Flow Manager in the controller. 0 - Indicates that the Flow Manager is disabled. 1 - Indicates that the Flow Manager is enabled. | 000 | Av | 50 | 0x0C_FlowMgrEnable , DA_Av ,050 ,Av ,050 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether or not to enabl ,
0x0C | 2 | 2 | FlowMonEnable | Byte |  | 51 |  |  |  | Value indicates whether or not to enable the Flow Monitor in the controller. 0 - Indicates that the Flow Manager is disabled. 1 - Indicates that the Flow Manager is enabled. | 000 | Av | 51 | 0x0C_FlowMonEnable , DA_Av ,051 ,Av ,051 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether or not to enabl ,
0x0C | 3 | 3 | WaterSourceEnable | Byte |  | 52 |  |  |  | Value indicates whether of not to enable MainSafes in the controller. 0 - Indicates that MainSafes are disabled. 1 - Indicates that MainSafes are enabled. | 000 | Av | 52 | 0x0C_WaterSourceEnable , DA_Av ,052 ,Av ,052 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether of not to enabl ,
000
0x0D – REPORT FLOW OPERATION PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x0D – REPORT FLOW OPERATION PARAMETERS
| demo=h0c.html | [9 empty] | 000
| template=type2.html | [9 empty] | 000
| This command will report the currnt firmware version of the Face Pack and all installed modules in the controller. | [9 empty] | 000
| When a response is received the payload of data is extracted and stored as shown below | [9 empty] | 000
000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x0D | 0 | 1 | FlowMgrEnable | Byte |  |  |  | 59 |  | Value indicates whether or not to enable the Flow Manager in the controller. 0 - Indicates that the Flow Manager is disabled. 1 - Indicates that the Flow Manager is enabled. | 000 | Ai | 59 | 0x0D_FlowMgrEnable , DA_Ai ,059 ,Ai ,059 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether or not to enabl ,
0x0D | 1 | 2 | FlowMonEnable | Byte |  |  |  | 60 |  | Value indicates whether or not to enable the Flow Monitor in the controller. 0 - Indicates that the Flow Manager is disabled. 1 - Indicates that the Flow Manager is enabled. | 000 | Ai | 60 | 0x0D_FlowMonEnable , DA_Ai ,060 ,Ai ,060 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether or not to enabl ,
0x0D | 2 | 3 | WaterSourceEnable | Byte |  |  |  | 61 |  | Value indicates whether of not to enable MainSafes in the controller. 0 - Indicates that MainSafes are disabled. 1 - Indicates that MainSafes are enabled. | 000 | Ai | 61 | 0x0D_WaterSourceEnable , DA_Ai ,061 ,Ai ,061 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether of not to enabl ,
000
0x0E – REPORT ITEM INFORMATION | [10 empty] | 000 |  |  |  |  | 0x0E – REPORT ITEM INFORMATION
| demo=h0e.html | [9 empty] | 000
| Template=None | [9 empty] | 000
| This command reports information regarding various items in the Controller to the Central. Items currently include Stations, P/MVs, and Sensor Decoders. | [9 empty] | 000
| Response data storage depends on the type of item being read | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x0E | 0 | 1 | Trigger_ReportItemInfo |  | 5 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 5 | 0x0E_Trigger_ReportItemInfo , DA_Bv ,005 ,Bv ,005 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x0E | 1 | 2 | ItemType | Byte |  | 53 |  |  |  | Contains the Item Type for which to return information. Range is 1 to 3. 1 = Station. 2 = P/MV. 3 = Sensor Decoder. | 000 | Av | 53 | 0x0E_ItemType , DA_Av ,053 ,Av ,053 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the Item Type for which to ret ,
0x0E | 2 | 3 | ItemID | UINT16 |  | 54 |  |  |  | Contains the number within the Item Type for which to start sending the information. May be Station Number- P/MV Number- or Sensor Decoder Address. Range is Item Type dependent. Station - Range is 1 to 225. P/MV - Range is 1 to 6. Sensor Decoer - Range is 1 to 9. | 000 | Av | 54 | 0x0E_ItemID , DA_Av ,054 ,Av ,054 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the number within the Item Typ ,
0x0E | if ( ItemType != 3 ) | [9 empty] | 000
0x0E | 3 | 4 | ItemType | Byte |  |  |  | 62 |  | Contains the Item Type for which to return information. Range is 1 to 3. 1 = Station. 2 = P/MV. 3 = Sensor Decoder. | 000 | Ai | 62 | 0x0E_ItemType , DA_Ai ,062 ,Ai ,062 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the Item Type for which to ret ,
0x0E | 4 | 5 | Count | Byte |  |  |  | 63 |  | Number of station paramters in this transmission. Range is dependent on ItemType. Station - Range is 1 to 35. P/MV - Range is 1 to 6. Sensor Decoder - Range is 1 to 9. | 000 | Ai | 63 | 0x0E_Count , DA_Ai ,063 ,Ai ,063 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Number of station paramters in this tra ,
0x0E | 5 | 6 | ItemID | UINT16 |  |  |  | 64 |  | Contains the number within the Item Type for which to start sending the information. May be Station Number- P/MV Number- or Sensor Decoder Address. Range is Item Type dependent. Station - Range is 1 to 225. P/MV - Range is 1 to 6. Sensor Decoer - Range is 1 to 9. | 000 | Ai | 64 | 0x0E_ItemID , DA_Ai ,064 ,Ai ,064 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the number within the Item Typ ,
0x0E | 6 | 7 | LoadPresent | Byte |  |  |  | 65 |  | Value indicates whether a load is present for the Station or P/MV. Range is 0 to 2. 0 - Load presence unknown. 1 - Load is not present. 2 - Load is present. | 000 | Ai | 65 | 0x0E_LoadPresent , DA_Ai ,065 ,Ai ,065 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a load is prese ,
0x0E | 7 | 8 | TurnOnCurrent | UINT16 |  |  |  | 66 |  | Actual current recorded for Station or P/MV last time it was turned on in mA. Range is 1023. | 000 | Ai | 66 | 0x0E_TurnOnCurrent , DA_Ai ,066 ,Ai ,066 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Actual current recorded for Station or ,
0x0E | 8 | 9 | DecPresence | Byte |  |  |  | 67 |  | Vaule indicating the decoder performed. Conventional controllers will return a vlue of 0 for this element and it should be ignored. | 000 | Ai | 67 | 0x0E_DecPresence , DA_Ai ,067 ,Ai ,067 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Vaule indicating the decoder performed. ,
0x0E | 9 | 10 | Comm | Byte |  |  |  | 68 |  | Decoder communications success rate in percent since the last power cycle. Range is 0 to 100- and 255. A value of 255 indicates that no communications have been attempted since the last power cycle. Conventional controllers will return a value of 0 for this element and it should be ignored | 000 | Ai | 68 | 0x0E_Comm , DA_Ai ,068 ,Ai ,068 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder communications success rate in ,
0x0E | else | [9 empty] | 000
0x0E | 5 | 4 | ItemID | UINT16 | [5 empty] | Contains the number within the Item Type for which to start sending the information. May be Station Number- P/MV Number- or Sensor Decoder Address. Range is Item Type dependent. Station - Range is 1 to 225. P/MV - Range is 1 to 6. Sensor Decoer - Range is 1 to 9. | 000
0x0E | 8 | 5 | DecPresence | Byte | [5 empty] | Vaule indicating the decoder performed. Conventional controllers will return a vlue of 0 for this element and it should be ignored. | 000
0x0E | 9 | 6 | Comm | Byte | [5 empty] | Decoder communications success rate in percent since the last power cycle. Range is 0 to 100- and 255. A value of 255 indicates that no communications have been attempted since the last power cycle. Conventional controllers will return a value of 0 for this element and it should be ignored | 000
000
0x10 – SET DECODER MODULE STATION ASSIGNMENTS (v2.00.016 and later) | [10 empty] | 000 |  |  |  |  | 0x10 – SET DECODER MODULE STATION ASSIGNMENTS (v2.00.016 and later)
| demo=h10.html | [9 empty] | 000
| Template=Type 1 | [9 empty] | 000
| This command sends the Station Assignments to be used by each of the Decoder Modules to the Controller. The Station Assignements are used to determine the Stations for which each Decoder Module is responsible for operating. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x10 | 0 | 1 | Trigger_SetDecodeModuleStnAssign |  | 6 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 6 | 0x10_Trigger_SetDecodeModuleStnAssign , DA_Bv ,006 ,Bv ,006 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x10 | 1 | 2 | Mod1LowerLimit | UINT16 |  | 55 |  |  |  | Contains Upper Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Av | 55 | 0x10_Mod1LowerLimit , DA_Av ,055 ,Av ,055 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Upper Station Limit for Decode ,
0x10 | 2 | 3 | Mod1UpperLimit | UINT16 |  | 56 |  |  |  | Contains Upper Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Av | 56 | 0x10_Mod1UpperLimit , DA_Av ,056 ,Av ,056 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Upper Station Limit for Decode ,
0x10 | 3 | 4 | Mod2LowerLimit | UINT16 |  | 57 |  |  |  | Contains Upper Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Av | 57 | 0x10_Mod2LowerLimit , DA_Av ,057 ,Av ,057 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Upper Station Limit for Decode ,
0x10 | 4 | 5 | Mod2UpperLimit | UINT16 |  | 58 |  |  |  | Contains Lower Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Av | 58 | 0x10_Mod2UpperLimit , DA_Av ,058 ,Av ,058 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Lower Station Limit for Decode ,
0x10 | 5 | 6 | Mod3LowerLimit | UINT16 |  | 59 |  |  |  | Contains Lower Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Av | 59 | 0x10_Mod3LowerLimit , DA_Av ,059 ,Av ,059 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Lower Station Limit for Decode ,
0x10 | 6 | 7 | Mod3UpperLimit | UINT16 |  | 60 |  |  |  | Contains Lower Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Av | 60 | 0x10_Mod3UpperLimit , DA_Av ,060 ,Av ,060 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Lower Station Limit for Decode ,
000
0x12 – SET ITEM NAMES (v2.00.016 and later) | [10 empty] | 000 |  |  |  |  | 0x12 – SET ITEM NAMES (v2.00.016 and later)
000
| This command sends the Item Name for the specified Item Type. Multiple Item Names may be sent in the command and they may be sent in any order. Item Names will only be sent up to their terminating character to allow the maximum number of names to be sent in a single transmission. | [9 empty] | 000
| acc2_option1 in the configuration sets the maximum length. The string sent to the ACC must be null terminated. Acc2_option1 is the max but we stop building the string when we encounter the 1st zero in the data array | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x12 | 0 | 1 | Trigger_SetItemNames |  | 7 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 7 | 0x12_Trigger_SetItemNames , DA_Bv ,007 ,Bv ,007 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x12 | Hard coded = 1 | 2 | Count | Byte |  | 61 |  |  |  | Contains the number of Item Names sent in this transmission. Range is 1 to 63. | 000 | Av | 61 | 0x12_Count , DA_Av ,061 ,Av ,061 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the number of Item Names sent ,
0x12 | 2 | 3 | ItemType | Byte |  | 62 |  |  |  | Value is the Item Type for which the name is being sent. Range is 1 to 6. 1 = Station Name- 2 = Block Name- 3 = Program Name- 4 = Clik Sensor- 5 = MainSafe- 6 = Flow Zone | 000 | Av | 62 | 0x12_ItemType , DA_Av ,062 ,Av ,062 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value is the Item Type for which the na ,
0x12 | 3 | 4 | ItemNumber | UINT16 |  | 63 |  |  |  | Value is the Item Number of the Item Type for which the name is being sent. Indicates Station Number- Program Number- etc. Range is Dependent on Item Type. Station Number = 1 to 225- Block Number = 1 to 64- Program Number = 1 to 32- Clik Sensor = 1 to 3- MainSafe = 1 to 6- Flow Zone = 1 to 6 | 000 | Av | 63 | 0x12_ItemNumber , DA_Av ,063 ,Av ,063 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value is the Item Number of the Item Ty ,
0x12 | 4 | 5 | ItemName[0] | Byte |  | 64 |  |  |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 must be used to indicate the end of the Item Name. Sending a name with a single character set to 0 will return name to default value. | 000 | Av | 64 | 0x12_ItemName[0] , DA_Av ,064 ,Av ,064 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x12 | 5 | 6 | ItemName[1] | Byte |  | 65 |  |  |  | ItemName[1] | 000 | Av | 65 | 0x12_ItemName[1] , DA_Av ,065 ,Av ,065 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[1] ,
0x12 | 6 | 7 | ItemName[2] | Byte |  | 66 |  |  |  | ItemName[2] | 000 | Av | 66 | 0x12_ItemName[2] , DA_Av ,066 ,Av ,066 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[2] ,
0x12 | 7 | 8 | ItemName[3] | Byte |  | 67 |  |  |  | ItemName[3] | 000 | Av | 67 | 0x12_ItemName[3] , DA_Av ,067 ,Av ,067 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[3] ,
0x12 | 8 | 9 | ItemName[4] | Byte |  | 68 |  |  |  | ItemName[4] | 000 | Av | 68 | 0x12_ItemName[4] , DA_Av ,068 ,Av ,068 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[4] ,
0x12 | 9 | 10 | ItemName[5] | Byte |  | 69 |  |  |  | ItemName[5] | 000 | Av | 69 | 0x12_ItemName[5] , DA_Av ,069 ,Av ,069 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[5] ,
0x12 | 10 | 11 | ItemName[6] | Byte |  | 70 |  |  |  | ItemName[6] | 000 | Av | 70 | 0x12_ItemName[6] , DA_Av ,070 ,Av ,070 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[6] ,
0x12 | 11 | 12 | ItemName[7] | Byte |  | 71 |  |  |  | ItemName[7] | 000 | Av | 71 | 0x12_ItemName[7] , DA_Av ,071 ,Av ,071 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[7] ,
0x12 | 12 | 13 | ItemName[8] | Byte |  | 72 |  |  |  | ItemName[8] | 000 | Av | 72 | 0x12_ItemName[8] , DA_Av ,072 ,Av ,072 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[8] ,
0x12 | 13 | 14 | ItemName[9] | Byte |  | 73 |  |  |  | ItemName[9] | 000 | Av | 73 | 0x12_ItemName[9] , DA_Av ,073 ,Av ,073 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[9] ,
0x12 | 14 | 15 | ItemName[10] | Byte |  | 74 |  |  |  | ItemName[10] | 000 | Av | 74 | 0x12_ItemName[10] , DA_Av ,074 ,Av ,074 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[10] ,
0x12 | 15 | 16 | ItemName[11] | Byte |  | 75 |  |  |  | ItemName[11] | 000 | Av | 75 | 0x12_ItemName[11] , DA_Av ,075 ,Av ,075 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[11] ,
0x12 | 16 | 17 | ItemName[12] | Byte |  | 76 |  |  |  | ItemName[12] | 000 | Av | 76 | 0x12_ItemName[12] , DA_Av ,076 ,Av ,076 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[12] ,
0x12 | 17 | 18 | ItemName[13] | Byte |  | 77 |  |  |  | ItemName[13] | 000 | Av | 77 | 0x12_ItemName[13] , DA_Av ,077 ,Av ,077 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[13] ,
0x12 | 18 | 19 | ItemName[14] | Byte |  | 78 |  |  |  | ItemName[14] | 000 | Av | 78 | 0x12_ItemName[14] , DA_Av ,078 ,Av ,078 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[14] ,
0x12 | 19 | 20 | ItemName[15] | Byte |  | 79 |  |  |  | ItemName[15] | 000 | Av | 79 | 0x12_ItemName[15] , DA_Av ,079 ,Av ,079 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[15] ,
0x12 | 20 | 21 | ItemName[16] | Byte |  | 80 |  |  |  | ItemName[16] | 000 | Av | 80 | 0x12_ItemName[16] , DA_Av ,080 ,Av ,080 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[16] ,
0x12 | 21 | 22 | ItemName[17] | Byte |  | 81 |  |  |  | ItemName[17] | 000 | Av | 81 | 0x12_ItemName[17] , DA_Av ,081 ,Av ,081 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[17] ,
0x12 | 22 | 23 | ItemName[18] | Byte |  | 82 |  |  |  | ItemName[18] | 000 | Av | 82 | 0x12_ItemName[18] , DA_Av ,082 ,Av ,082 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[18] ,
0x12 | 23 | 24 | ItemName[19] | Byte |  | 83 |  |  |  | ItemName[19] | 000 | Av | 83 | 0x12_ItemName[19] , DA_Av ,083 ,Av ,083 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[19] ,
0x12 | 24 | 25 | ItemName[20] | Byte |  | 84 |  |  |  | ItemName[20] | 000 | Av | 84 | 0x12_ItemName[20] , DA_Av ,084 ,Av ,084 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[20] ,
0x12 | 25 | 26 | ItemName[21] | Byte |  | 85 |  |  |  | ItemName[21] | 000 | Av | 85 | 0x12_ItemName[21] , DA_Av ,085 ,Av ,085 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[21] ,
0x12 | 26 | 27 | ItemName[22] | Byte |  | 86 |  | says |  | ItemName[22] | 000 | Av | 86 | 0x12_ItemName[22] , DA_Av ,086 ,Av ,086 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[22] ,
0x12 | 27 | 28 | ItemName[23] | Byte |  | 87 |  |  |  | ItemName[23] | 000 | Av | 87 | 0x12_ItemName[23] , DA_Av ,087 ,Av ,087 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[23] ,
0x12 | 28 | 29 | ItemName[24] | Byte |  | 88 |  |  |  | ItemName[24] | 000 | Av | 88 | 0x12_ItemName[24] , DA_Av ,088 ,Av ,088 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[24] ,
0x12 | 29 | 30 | ItemName[25] | Byte |  | 89 |  |  |  | ItemName[25] | 000 | Av | 89 | 0x12_ItemName[25] , DA_Av ,089 ,Av ,089 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,ItemName[25] ,
000
000
000
0x13 – SET STATION PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x13 – SET STATION PARAMETERS
| demo=h13 | [9 empty] | 000
| Template=Type1 | [9 empty] | 000
| Partner service : | 0x33 – REPORT STATION PARAMETERS (v.2.00.016 and later) | [8 empty] | 000
| This command sends all station level parameters from the central to the controller | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x13 | 0 |  | Trigger_SetStnParams |  | 8 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 8 | 0x13_Trigger_SetStnParams , DA_Bv ,008 ,Bv ,008 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x13 | Hard coded = 1 | 1 | Count | Byte |  | 90 |  |  |  | Number of station paramters in this transmission. Range is 1 to 18. | 000 | Av | 90 | 0x13_Count , DA_Av ,090 ,Av ,090 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Number of station paramters in this tra ,
0x13 | 2 | 2 | Station# | UINT16 |  | 91 |  |  |  | Part of Station Parameters. Contains the Station Number for the parameters being sent. Range is 1 to 225. | 000 | Av | 91 | 0x13_Station# , DA_Av ,091 ,Av ,091 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x13 | 3 | 3 | PumpUsage | Byte |  | 92 |  |  |  | Part of Station Parameters. Value containing information on the pumps required to operate when the station is active. Bit 0: 1 = Pump 1 used- 0 = Pump 1 Not used. Bit 1: 1 = Pump 2 used- 0 = Pump 2 Not used. Bit 2: 1 = Pump 3 used- 0 = Pump 3 Not used. Bit 3: 1 = Pump 4 used- 0 = Pump 4 Not used. Bit 4: 1 = Pump 5 used- 0 = Pump 5 Not used. Bit 5: 1 = Pump 6 used- 0 = Pump 6 Not used. | 000 | Av | 92 | 0x13_PumpUsage , DA_Av ,092 ,Av ,092 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Value conta ,
0x13 | 4 | 4 | CycleTime | UINT16 |  | 93 |  |  |  | Part of Station Parameters. Contains the maximum number of minutes to allow for a single cycle for the specified station. Rnage is 1 to 360. Not used is indicated by 0. If Cycle Rime is 0- the Soak Time will be forced to 0 regardless of value sent in command. | 000 | Av | 93 | 0x13_CycleTime , DA_Av ,093 ,Av ,093 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x13 | 5 | 5 | SoakTime | UINT16 |  | 94 |  |  |  | Part of Station Parameters. Contains the minimum soak time before a subsequent cycle can begin for a station. Range is 1 to 540. Not used is indicated by 0. | 000 | Av | 94 | 0x13_SoakTime , DA_Av ,094 ,Av ,094 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x13 | 6 | 6 | FlowZone | Byte |  | 95 |  |  |  | Part of Station Parameters. Contains the Flow Zone number that the station is assigned to. Range is 0 to 6. A value of 0 indicated that the station is not assigned to a Flow Zone. | 000 | Av | 95 | 0x13_FlowZone , DA_Av ,095 ,Av ,095 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x13 | 7 | 7 | FlowPriority | Byte |  | 96 |  |  |  | Part of Station Parameters. Contains indication of whether or not this station is a Flow Priority. A value of 0 indicated no priority. A value of 1 indicated that it is a Flow Priority. | 000 | Av | 96 | 0x13_FlowPriority , DA_Av ,096 ,Av ,096 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains in ,
0x13 | 8 | 8 | LearnedFlow | UINT16 |  | 97 |  |  |  | Part of Station Parameters. Contains the learned flow value for the station times 10. Value is in gallons and the range is 1 to 6-550.0 in steps of 0.1. A value of 0xFFEF indicates to ignore Learned Flow value for this Station. A value of 0xFFFF indicates that the station is not learned and is the default value. | 000 | Av | 97 | 0x13_LearnedFlow , DA_Av ,097 ,Av ,097 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x13 | 9 | 9 | FlowDelay | UINT16 |  | 98 |  |  |  | Part of Station Parameters. Contains the delay tie in seconds before beginning to start flow monitoring for that station. Rance is 15 to 600. Default is 60. | 000 | Av | 98 | 0x13_FlowDelay , DA_Av ,098 ,Av ,098 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
000
0x15 – REPORT DECODER MODULE STATION ASSIGNMENTS (v2.00.016 and later) | [10 empty] | 000 |  |  |  |  | 0x15 – REPORT DECODER MODULE STATION ASSIGNMENTS (v2.00.016 and later)
| demo=h10.html | [9 empty] | 000
| Template=Type 1 | [9 empty] | 000
| This command sends the Station Assignments to be used by each of the Decoder Modules that are stored in the Controller to the Central. The Station Assignments are used to determine the Stations for which each Decoder Module is responsible for operating. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x15 | 0 | 2 | Mod1LowerLimit | UINT16 |  |  |  | 1288 |  | Contains Upper Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Ai | 1288 | 0x15_Mod1LowerLimit , DA_Ai ,1288 ,Ai ,1288 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Upper Station Limit for Decode ,
0x15 | 1 | 3 | Mod1UpperLimit | UINT16 |  |  |  | 1289 |  | Contains Upper Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Ai | 1289 | 0x15_Mod1UpperLimit , DA_Ai ,1289 ,Ai ,1289 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Upper Station Limit for Decode ,
0x15 | 2 | 4 | Mod2LowerLimit | UINT16 |  |  |  | 1290 |  | Contains Upper Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Ai | 1290 | 0x15_Mod2LowerLimit , DA_Ai ,1290 ,Ai ,1290 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Upper Station Limit for Decode ,
0x15 | 3 | 5 | Mod2UpperLimit | UINT16 |  |  |  | 1291 |  | Contains Lower Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Ai | 1291 | 0x15_Mod2UpperLimit , DA_Ai ,1291 ,Ai ,1291 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Lower Station Limit for Decode ,
0x15 | 4 | 6 | Mod3LowerLimit | UINT16 |  |  |  | 1292 |  | Contains Lower Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Ai | 1292 | 0x15_Mod3LowerLimit , DA_Ai ,1292 ,Ai ,1292 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Lower Station Limit for Decode ,
0x15 | 5 | 7 | Mod3UpperLimit | UINT16 |  |  |  | 1293 |  | Contains Lower Station Limit for Decoder Module X. Range is 0 to 225. | 000 | Ai | 1293 | 0x15_Mod3UpperLimit , DA_Ai ,1293 ,Ai ,1293 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains Lower Station Limit for Decode ,
000
0x16 - Set Pump / Master Valve Param | [10 empty] | 000 |  |  |  |  | 0x16 - Set Pump / Master Valve Param
| Not implemented (yet) | [9 empty] | 000
000
000
0x17 – SET MAINSAFE PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x17 – SET MAINSAFE PARAMETERS
| demo=h17.html | [9 empty] | 000
| Template=Type 1 | [9 empty] | 000
| This command sends all station level parameters from the central to the controller | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x17 | 0 |  | Trigger_SetMainSafe |  | 9 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 9 | 0x17_Trigger_SetMainSafe , DA_Bv ,009 ,Bv ,009 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x17 | 1 | 1 | PMV | Byte |  | 99 |  |  | Ms01 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Av | 99 | 0x17_Ms01PMV , DA_Av ,099 ,Av ,099 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x17 | 2 | 2 | FlowSen | Byte |  | 100 |  |  | Ms01 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Av | 100 | 0x17_Ms01FlowSen , DA_Av ,100 ,Av ,100 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x17 | 3 | 3 | MonitorEnable | Byte |  | 101 |  |  | Ms01 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Av | 101 | 0x17_Ms01MonitorEnable , DA_Av ,101 ,Av ,101 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x17 | 4 | 4 | MaxFlowLimit | UINT32 |  | 102 |  |  | Ms01 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 102 | 0x17_Ms01MaxFlowLimit , DA_Av ,102 ,Av ,102 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x17 | 5 | 5 | UnschedFlowLimit | UINT32 |  | 103 |  |  | Ms01 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 103 | 0x17_Ms01UnschedFlowLimit , DA_Av ,103 ,Av ,103 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x17 | 6 | 6 | AlarmSetDelay | UINT16 |  | 104 |  |  | Ms01 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Av | 104 | 0x17_Ms01AlarmSetDelay , DA_Av ,104 ,Av ,104 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x17 | 8 | 7 | AlarmClearDelay | UINT32 |  | 105 |  |  | Ms01 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Av | 105 | 0x17_Ms01AlarmClearDelay , DA_Av ,105 ,Av ,105 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x17 | 9 | 8 | MonthlyBudget | UINT32 |  | 106 |  |  | Ms01 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Av | 106 | 0x17_Ms01MonthlyBudget , DA_Av ,106 ,Av ,106 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x17 | 9 | 9 | ManualAllowance | UINT16 |  | 107 |  |  | Ms01 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Av | 107 | 0x17_Ms01ManualAllowance , DA_Av ,107 ,Av ,107 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x17 | 10 | 10 | PMV | Byte |  | 108 |  |  | Ms02 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Av | 108 | 0x17_Ms02PMV , DA_Av ,108 ,Av ,108 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x17 | 11 | 11 | FlowSen | Byte |  | 109 |  |  | Ms02 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Av | 109 | 0x17_Ms02FlowSen , DA_Av ,109 ,Av ,109 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x17 | 12 | 12 | MonitorEnable | Byte |  | 110 |  |  | Ms02 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Av | 110 | 0x17_Ms02MonitorEnable , DA_Av ,110 ,Av ,110 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x17 | 13 | 13 | MaxFlowLimit | UINT32 |  | 111 |  |  | Ms02 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 111 | 0x17_Ms02MaxFlowLimit , DA_Av ,111 ,Av ,111 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x17 | 14 | 14 | UnschedFlowLimit | UINT32 |  | 112 |  |  | Ms02 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 112 | 0x17_Ms02UnschedFlowLimit , DA_Av ,112 ,Av ,112 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x17 | 15 | 15 | AlarmSetDelay | UINT16 |  | 113 |  |  | Ms02 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Av | 113 | 0x17_Ms02AlarmSetDelay , DA_Av ,113 ,Av ,113 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x17 | 16 | 16 | AlarmClearDelay | UINT32 |  | 114 |  |  | Ms02 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Av | 114 | 0x17_Ms02AlarmClearDelay , DA_Av ,114 ,Av ,114 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x17 | 17 | 17 | MonthlyBudget | UINT32 |  | 115 |  |  | Ms02 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Av | 115 | 0x17_Ms02MonthlyBudget , DA_Av ,115 ,Av ,115 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x17 | 18 | 18 | ManualAllowance | UINT16 |  | 116 |  |  | Ms02 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Av | 116 | 0x17_Ms02ManualAllowance , DA_Av ,116 ,Av ,116 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x17 | 19 | 19 | PMV | Byte |  | 117 |  |  | Ms03 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Av | 117 | 0x17_Ms03PMV , DA_Av ,117 ,Av ,117 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x17 | 20 | 20 | FlowSen | Byte |  | 118 |  |  | Ms03 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Av | 118 | 0x17_Ms03FlowSen , DA_Av ,118 ,Av ,118 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x17 | 21 | 21 | MonitorEnable | Byte |  | 119 |  |  | Ms03 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Av | 119 | 0x17_Ms03MonitorEnable , DA_Av ,119 ,Av ,119 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x17 | 22 | 22 | MaxFlowLimit | UINT32 |  | 120 |  |  | Ms03 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 120 | 0x17_Ms03MaxFlowLimit , DA_Av ,120 ,Av ,120 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x17 | 23 | 23 | UnschedFlowLimit | UINT32 |  | 121 |  |  | Ms03 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 121 | 0x17_Ms03UnschedFlowLimit , DA_Av ,121 ,Av ,121 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x17 | 24 | 24 | AlarmSetDelay | UINT16 |  | 122 |  |  | Ms03 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Av | 122 | 0x17_Ms03AlarmSetDelay , DA_Av ,122 ,Av ,122 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x17 | 25 | 25 | AlarmClearDelay | UINT32 |  | 123 |  |  | Ms03 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Av | 123 | 0x17_Ms03AlarmClearDelay , DA_Av ,123 ,Av ,123 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x17 | 26 | 26 | MonthlyBudget | UINT32 |  | 124 |  |  | Ms03 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Av | 124 | 0x17_Ms03MonthlyBudget , DA_Av ,124 ,Av ,124 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x17 | 27 | 27 | ManualAllowance | UINT16 |  | 125 |  |  | Ms03 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Av | 125 | 0x17_Ms03ManualAllowance , DA_Av ,125 ,Av ,125 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x17 | 28 | 28 | PMV | Byte |  | 126 |  |  | Ms04 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Av | 126 | 0x17_Ms04PMV , DA_Av ,126 ,Av ,126 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x17 | 29 | 29 | FlowSen | Byte |  | 127 |  |  | Ms04 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Av | 127 | 0x17_Ms04FlowSen , DA_Av ,127 ,Av ,127 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x17 | 30 | 30 | MonitorEnable | Byte |  | 128 |  |  | Ms04 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Av | 128 | 0x17_Ms04MonitorEnable , DA_Av ,128 ,Av ,128 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x17 | 31 | 31 | MaxFlowLimit | UINT32 |  | 129 |  |  | Ms04 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 129 | 0x17_Ms04MaxFlowLimit , DA_Av ,129 ,Av ,129 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x17 | 32 | 32 | UnschedFlowLimit | UINT32 |  | 130 |  |  | Ms04 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 130 | 0x17_Ms04UnschedFlowLimit , DA_Av ,130 ,Av ,130 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x17 | 33 | 33 | AlarmSetDelay | UINT16 |  | 131 |  |  | Ms04 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Av | 131 | 0x17_Ms04AlarmSetDelay , DA_Av ,131 ,Av ,131 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x17 | 34 | 34 | AlarmClearDelay | UINT32 |  | 132 |  |  | Ms04 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Av | 132 | 0x17_Ms04AlarmClearDelay , DA_Av ,132 ,Av ,132 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x17 | 35 | 35 | MonthlyBudget | UINT32 |  | 133 |  |  | Ms04 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Av | 133 | 0x17_Ms04MonthlyBudget , DA_Av ,133 ,Av ,133 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x17 | 36 | 36 | ManualAllowance | UINT16 |  | 134 |  |  | Ms04 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Av | 134 | 0x17_Ms04ManualAllowance , DA_Av ,134 ,Av ,134 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x17 | 37 | 37 | PMV | Byte |  | 135 |  |  | Ms05 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Av | 135 | 0x17_Ms05PMV , DA_Av ,135 ,Av ,135 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x17 | 38 | 38 | FlowSen | Byte |  | 136 |  |  | Ms05 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Av | 136 | 0x17_Ms05FlowSen , DA_Av ,136 ,Av ,136 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x17 | 39 | 39 | MonitorEnable | Byte |  | 137 |  |  | Ms05 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Av | 137 | 0x17_Ms05MonitorEnable , DA_Av ,137 ,Av ,137 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x17 | 40 | 40 | MaxFlowLimit | UINT32 |  | 138 |  |  | Ms05 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 138 | 0x17_Ms05MaxFlowLimit , DA_Av ,138 ,Av ,138 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x17 | 41 | 41 | UnschedFlowLimit | UINT32 |  | 139 |  |  | Ms05 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 139 | 0x17_Ms05UnschedFlowLimit , DA_Av ,139 ,Av ,139 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x17 | 42 | 42 | AlarmSetDelay | UINT16 |  | 140 |  |  | Ms05 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Av | 140 | 0x17_Ms05AlarmSetDelay , DA_Av ,140 ,Av ,140 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x17 | 43 | 43 | AlarmClearDelay | UINT32 |  | 141 |  |  | Ms05 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Av | 141 | 0x17_Ms05AlarmClearDelay , DA_Av ,141 ,Av ,141 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x17 | 44 | 44 | MonthlyBudget | UINT32 |  | 142 |  |  | Ms05 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Av | 142 | 0x17_Ms05MonthlyBudget , DA_Av ,142 ,Av ,142 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x17 | 45 | 45 | ManualAllowance | UINT16 |  | 143 |  |  | Ms05 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Av | 143 | 0x17_Ms05ManualAllowance , DA_Av ,143 ,Av ,143 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x17 | 46 | 46 | PMV | Byte |  | 144 |  |  | Ms06 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Av | 144 | 0x17_Ms06PMV , DA_Av ,144 ,Av ,144 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x17 | 47 | 47 | FlowSen | Byte |  | 145 |  |  | Ms06 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Av | 145 | 0x17_Ms06FlowSen , DA_Av ,145 ,Av ,145 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x17 | 48 | 48 | MonitorEnable | Byte |  | 146 |  |  | Ms06 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Av | 146 | 0x17_Ms06MonitorEnable , DA_Av ,146 ,Av ,146 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x17 | 49 | 49 | MaxFlowLimit | UINT32 |  | 147 |  |  | Ms06 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 147 | 0x17_Ms06MaxFlowLimit , DA_Av ,147 ,Av ,147 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x17 | 50 | 50 | UnschedFlowLimit | UINT32 |  | 148 |  |  | Ms06 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 148 | 0x17_Ms06UnschedFlowLimit , DA_Av ,148 ,Av ,148 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x17 | 51 | 51 | AlarmSetDelay | UINT16 |  | 149 |  |  | Ms06 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Av | 149 | 0x17_Ms06AlarmSetDelay , DA_Av ,149 ,Av ,149 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x17 | 52 | 52 | AlarmClearDelay | UINT32 |  | 150 |  |  | Ms06 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Av | 150 | 0x17_Ms06AlarmClearDelay , DA_Av ,150 ,Av ,150 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x17 | 53 | 53 | MonthlyBudget | UINT32 |  | 151 |  |  | Ms06 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Av | 151 | 0x17_Ms06MonthlyBudget , DA_Av ,151 ,Av ,151 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x17 | 54 | 54 | ManualAllowance | UINT16 |  | 152 |  |  | Ms06 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Av | 152 | 0x17_Ms06ManualAllowance , DA_Av ,152 ,Av ,152 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
000
0x18 – REPORT MAINSAFE PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x18 – REPORT MAINSAFE PARAMETERS
| demo=h17.html | [9 empty] | 000
| Template=Type 1 | [9 empty] | 000
| This command reports all MainSafe settings for each of the six MainSafes fom the controller to the central. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x18 | 0 | 1 | PMV | Byte |  |  |  | 69 | Ms01 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Ai | 69 | 0x18_Ms01PMV , DA_Ai ,069 ,Ai ,069 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x18 | 1 | 2 | FlowSen | Byte |  |  |  | 70 | Ms01 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Ai | 70 | 0x18_Ms01FlowSen , DA_Ai ,070 ,Ai ,070 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x18 | 2 | 3 | MonitorEnable | Byte |  |  |  | 71 | Ms01 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Ai | 71 | 0x18_Ms01MonitorEnable , DA_Ai ,071 ,Ai ,071 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x18 | 3 | 4 | MaxFlowLimit | UINT32 |  |  |  | 72 | Ms01 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 72 | 0x18_Ms01MaxFlowLimit , DA_Ai ,072 ,Ai ,072 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x18 | 4 | 5 | UnschedFlowLimit | UINT32 |  |  |  | 73 | Ms01 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 73 | 0x18_Ms01UnschedFlowLimit , DA_Ai ,073 ,Ai ,073 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x18 | 5 | 6 | AlarmSetDelay | UINT16 |  |  |  | 74 | Ms01 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Ai | 74 | 0x18_Ms01AlarmSetDelay , DA_Ai ,074 ,Ai ,074 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x18 | 6 | 7 | AlarmClearDelay | UINT32 |  |  |  | 75 | Ms01 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Ai | 75 | 0x18_Ms01AlarmClearDelay , DA_Ai ,075 ,Ai ,075 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x18 | 7 | 8 | MonthlyBudget | UINT32 |  |  |  | 76 | Ms01 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Ai | 76 | 0x18_Ms01MonthlyBudget , DA_Ai ,076 ,Ai ,076 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x18 | 8 | 9 | ManualAllowance | UINT16 |  |  |  | 77 | Ms01 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Ai | 77 | 0x18_Ms01ManualAllowance , DA_Ai ,077 ,Ai ,077 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x18 | 9 | 10 | PMV | Byte |  |  |  | 78 | Ms02 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Ai | 78 | 0x18_Ms02PMV , DA_Ai ,078 ,Ai ,078 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x18 | 10 | 11 | FlowSen | Byte |  |  |  | 79 | Ms02 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Ai | 79 | 0x18_Ms02FlowSen , DA_Ai ,079 ,Ai ,079 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x18 | 11 | 12 | MonitorEnable | Byte |  |  |  | 80 | Ms02 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Ai | 80 | 0x18_Ms02MonitorEnable , DA_Ai ,080 ,Ai ,080 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x18 | 12 | 13 | MaxFlowLimit | UINT32 |  |  |  | 81 | Ms02 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 81 | 0x18_Ms02MaxFlowLimit , DA_Ai ,081 ,Ai ,081 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x18 | 13 | 14 | UnschedFlowLimit | UINT32 |  |  |  | 82 | Ms02 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 82 | 0x18_Ms02UnschedFlowLimit , DA_Ai ,082 ,Ai ,082 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x18 | 14 | 15 | AlarmSetDelay | UINT16 |  |  |  | 83 | Ms02 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Ai | 83 | 0x18_Ms02AlarmSetDelay , DA_Ai ,083 ,Ai ,083 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x18 | 15 | 16 | AlarmClearDelay | UINT32 |  |  |  | 84 | Ms02 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Ai | 84 | 0x18_Ms02AlarmClearDelay , DA_Ai ,084 ,Ai ,084 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x18 | 16 | 17 | MonthlyBudget | UINT32 |  |  |  | 85 | Ms02 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Ai | 85 | 0x18_Ms02MonthlyBudget , DA_Ai ,085 ,Ai ,085 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x18 | 17 | 18 | ManualAllowance | UINT16 |  |  |  | 86 | Ms02 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Ai | 86 | 0x18_Ms02ManualAllowance , DA_Ai ,086 ,Ai ,086 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x18 | 18 | 19 | PMV | Byte |  |  |  | 87 | Ms03 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Ai | 87 | 0x18_Ms03PMV , DA_Ai ,087 ,Ai ,087 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x18 | 19 | 20 | FlowSen | Byte |  |  |  | 88 | Ms03 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Ai | 88 | 0x18_Ms03FlowSen , DA_Ai ,088 ,Ai ,088 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x18 | 20 | 21 | MonitorEnable | Byte |  |  |  | 89 | Ms03 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Ai | 89 | 0x18_Ms03MonitorEnable , DA_Ai ,089 ,Ai ,089 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x18 | 21 | 22 | MaxFlowLimit | UINT32 |  |  |  | 90 | Ms03 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 90 | 0x18_Ms03MaxFlowLimit , DA_Ai ,090 ,Ai ,090 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x18 | 22 | 23 | UnschedFlowLimit | UINT32 |  |  |  | 91 | Ms03 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 91 | 0x18_Ms03UnschedFlowLimit , DA_Ai ,091 ,Ai ,091 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x18 | 23 | 24 | AlarmSetDelay | UINT16 |  |  |  | 92 | Ms03 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Ai | 92 | 0x18_Ms03AlarmSetDelay , DA_Ai ,092 ,Ai ,092 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x18 | 24 | 25 | AlarmClearDelay | UINT32 |  |  |  | 93 | Ms03 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Ai | 93 | 0x18_Ms03AlarmClearDelay , DA_Ai ,093 ,Ai ,093 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x18 | 25 | 26 | MonthlyBudget | UINT32 |  |  |  | 94 | Ms03 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Ai | 94 | 0x18_Ms03MonthlyBudget , DA_Ai ,094 ,Ai ,094 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x18 | 26 | 27 | ManualAllowance | UINT16 |  |  |  | 95 | Ms03 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Ai | 95 | 0x18_Ms03ManualAllowance , DA_Ai ,095 ,Ai ,095 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x18 | 27 | 28 | PMV | Byte |  |  |  | 96 | Ms04 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Ai | 96 | 0x18_Ms04PMV , DA_Ai ,096 ,Ai ,096 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x18 | 28 | 29 | FlowSen | Byte |  |  |  | 97 | Ms04 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Ai | 97 | 0x18_Ms04FlowSen , DA_Ai ,097 ,Ai ,097 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x18 | 29 | 30 | MonitorEnable | Byte |  |  |  | 98 | Ms04 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Ai | 98 | 0x18_Ms04MonitorEnable , DA_Ai ,098 ,Ai ,098 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x18 | 30 | 31 | MaxFlowLimit | UINT32 |  |  |  | 99 | Ms04 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 99 | 0x18_Ms04MaxFlowLimit , DA_Ai ,099 ,Ai ,099 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x18 | 31 | 32 | UnschedFlowLimit | UINT32 |  |  |  | 100 | Ms04 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 100 | 0x18_Ms04UnschedFlowLimit , DA_Ai ,100 ,Ai ,100 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x18 | 32 | 33 | AlarmSetDelay | UINT16 |  |  |  | 101 | Ms04 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Ai | 101 | 0x18_Ms04AlarmSetDelay , DA_Ai ,101 ,Ai ,101 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x18 | 33 | 34 | AlarmClearDelay | UINT32 |  |  |  | 102 | Ms04 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Ai | 102 | 0x18_Ms04AlarmClearDelay , DA_Ai ,102 ,Ai ,102 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x18 | 34 | 35 | MonthlyBudget | UINT32 |  |  |  | 103 | Ms04 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Ai | 103 | 0x18_Ms04MonthlyBudget , DA_Ai ,103 ,Ai ,103 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x18 | 35 | 36 | ManualAllowance | UINT16 |  |  |  | 104 | Ms04 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Ai | 104 | 0x18_Ms04ManualAllowance , DA_Ai ,104 ,Ai ,104 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x18 | 36 | 37 | PMV | Byte |  |  |  | 105 | Ms05 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Ai | 105 | 0x18_Ms05PMV , DA_Ai ,105 ,Ai ,105 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x18 | 37 | 38 | FlowSen | Byte |  |  |  | 106 | Ms05 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Ai | 106 | 0x18_Ms05FlowSen , DA_Ai ,106 ,Ai ,106 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x18 | 38 | 39 | MonitorEnable | Byte |  |  |  | 107 | Ms05 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Ai | 107 | 0x18_Ms05MonitorEnable , DA_Ai ,107 ,Ai ,107 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x18 | 39 | 40 | MaxFlowLimit | UINT32 |  |  |  | 108 | Ms05 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 108 | 0x18_Ms05MaxFlowLimit , DA_Ai ,108 ,Ai ,108 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x18 | 40 | 41 | UnschedFlowLimit | UINT32 |  |  |  | 109 | Ms05 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 109 | 0x18_Ms05UnschedFlowLimit , DA_Ai ,109 ,Ai ,109 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x18 | 41 | 42 | AlarmSetDelay | UINT16 |  |  |  | 110 | Ms05 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Ai | 110 | 0x18_Ms05AlarmSetDelay , DA_Ai ,110 ,Ai ,110 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x18 | 42 | 43 | AlarmClearDelay | UINT32 |  |  |  | 111 | Ms05 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Ai | 111 | 0x18_Ms05AlarmClearDelay , DA_Ai ,111 ,Ai ,111 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x18 | 43 | 44 | MonthlyBudget | UINT32 |  |  |  | 112 | Ms05 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Ai | 112 | 0x18_Ms05MonthlyBudget , DA_Ai ,112 ,Ai ,112 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x18 | 44 | 45 | ManualAllowance | UINT16 |  |  |  | 113 | Ms05 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Ai | 113 | 0x18_Ms05ManualAllowance , DA_Ai ,113 ,Ai ,113 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
0x18 | 45 | 46 | PMV | Byte |  |  |  | 114 | Ms06 | Master valve number to assign to this MainSafe. Ranse is 0 to 6. | 000 | Ai | 114 | 0x18_Ms06PMV , DA_Ai ,114 ,Ai ,114 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Master valve number to assign to this M ,
0x18 | 46 | 47 | FlowSen | Byte |  |  |  | 115 | Ms06 | Flow sensor number to assign to this MainSafe. Range is 0 to 6. | 000 | Ai | 115 | 0x18_Ms06FlowSen , DA_Ai ,115 ,Ai ,115 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow sensor number to assign to this Ma ,
0x18 | 47 | 48 | MonitorEnable | Byte |  |  |  | 116 | Ms06 | Enable monitoring for this MainSafe. Range is 0 to 1. | 000 | Ai | 116 | 0x18_Ms06MonitorEnable , DA_Ai ,116 ,Ai ,116 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable monitoring for this MainSafe. R ,
0x18 | 48 | 49 | MaxFlowLimit | UINT32 |  |  |  | 117 | Ms06 | Maximum flow limit for this MainSafe times 10. Value of GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 117 | 0x18_Ms06MaxFlowLimit , DA_Ai ,117 ,Ai ,117 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this MainSafe ti ,
0x18 | 49 | 50 | UnschedFlowLimit | UINT32 |  |  |  | 118 | Ms06 | Unscheduled flow limit for this MainSafe time 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 118 | 0x18_Ms06UnschedFlowLimit , DA_Ai ,118 ,Ai ,118 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this MainSaf ,
0x18 | 50 | 51 | AlarmSetDelay | UINT16 |  |  |  | 119 | Ms06 | Amount of time that the MainSafe must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9:59 m:ss). Default is 180 (3:00 m:ss) | 000 | Ai | 119 | 0x18_Ms06AlarmSetDelay , DA_Ai ,119 ,Ai ,119 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of time that the MainSafe must b ,
0x18 | 51 | 52 | AlarmClearDelay | UINT32 |  |  |  | 120 | Ms06 | Time after a MainSafe alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm) | 000 | Ai | 120 | 0x18_Ms06AlarmClearDelay , DA_Ai ,120 ,Ai ,120 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a MainSafe alarm is detected ,
0x18 | 52 | 53 | MonthlyBudget | UINT32 |  |  |  | 121 | Ms06 | Monthly water budget for this MainSafe times 10. Value is in gallons and the range is 0 to 10-000-000.0 insteps of 0.1. | 000 | Ai | 121 | 0x18_Ms06MonthlyBudget , DA_Ai ,121 ,Ai ,121 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this MainSafe ,
0x18 | 53 | 54 | ManualAllowance | UINT16 |  |  |  | 122 | Ms06 | Amount of manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is in GPM. Range is 6-550.0 in steps of 0.1. | 000 | Ai | 122 | 0x18_Ms06ManualAllowance , DA_Ai ,122 ,Ai ,122 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Amount of manual water (quick couplers- ,
000
0x19 – SET FLOW ZONE PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x19 – SET FLOW ZONE PARAMETERS
| demo=h19.html | [9 empty] | 000
| Template=Type 1 | [9 empty] | 000
| This command sends all Flow Zone Parametes to the controller. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x19 | 0 |  | Trigger_SetFlowZones |  | 10 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 10 | 0x19_Trigger_SetFlowZones , DA_Bv ,010 ,Bv ,010 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x19 | 1 | 1 | FlowMgrEnable | Byte |  | 153 |  |  | Fz01 | Enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 153 | 0x19_Fz01FlowMgrEnable , DA_Av ,153 ,Av ,153 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Manager for this Flow Z ,
0x19 | 2 | 2 | FlowTarget | UINT32 |  | 154 |  |  | Fz01 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 154 | 0x19_Fz01FlowTarget , DA_Av ,154 ,Av ,154 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x19 | 3 | 3 | FlowMonEnable | Byte |  | 155 |  |  | Fz01 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 155 | 0x19_Fz01FlowMonEnable , DA_Av ,155 ,Av ,155 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x19 | 4 | 4 | MaxPOverflow | UINT16 |  | 156 |  |  | Fz01 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Av | 156 | 0x19_Fz01MaxPOverflow , DA_Av ,156 ,Av ,156 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x19 | 5 | 5 | MaxPUnderflow | UINT16 |  | 157 |  |  | Fz01 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Av | 157 | 0x19_Fz01MaxPUnderflow , DA_Av ,157 ,Av ,157 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x19 | 6 | 6 | FlowSenMap | Byte |  | 158 |  |  | Fz01 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Av | 158 | 0x19_Fz01FlowSenMap , DA_Av ,158 ,Av ,158 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x19 | 7 | 7 | PmvMap | Byte |  | 159 |  |  | Fz01 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Av | 159 | 0x19_Fz01PmvMap , DA_Av ,159 ,Av ,159 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x19 | 8 | 8 | WsAssign | Byte |  | 160 |  |  | Fz01 | Info on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Av | 160 | 0x19_Fz01WsAssign , DA_Av ,160 ,Av ,160 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info on the MainSafe to which this Flow ,
0x19 | 9 | 9 | MonthlyBudget | UINT32 |  | 161 |  |  | Fz01 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Av | 161 | 0x19_Fz01MonthlyBudget , DA_Av ,161 ,Av ,161 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x19 | 10 | 10 | ManualAllowance | UINT16 |  | 162 |  |  | Fz01 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Av | 162 | 0x19_Fz01ManualAllowance , DA_Av ,162 ,Av ,162 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x19 | 11 | 11 | MaxFlowLimit | UINT32 |  | 163 |  |  | Fz01 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Av | 163 | 0x19_Fz01MaxFlowLimit , DA_Av ,163 ,Av ,163 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x19 | 12 | 12 | UnschedFlowLimit | UINT32 |  | 164 |  |  | Fz01 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 164 | 0x19_Fz01UnschedFlowLimit , DA_Av ,164 ,Av ,164 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x19 | 13 | 13 | AlarmSetDelay | UINT16 |  | 165 |  |  | Fz01 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Av | 165 | 0x19_Fz01AlarmSetDelay , DA_Av ,165 ,Av ,165 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x19 | 14 | 14 | AlarmClearDelay | UINT32 |  | 166 |  |  | Fz01 | Time after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Av | 166 | 0x19_Fz01AlarmClearDelay , DA_Av ,166 ,Av ,166 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a Flow Zone alarm is detecte ,
0x19 | 15 | 15 | FlowMgrEnable | Byte |  | 167 |  |  | Fz02 | Enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 167 | 0x19_Fz02FlowMgrEnable , DA_Av ,167 ,Av ,167 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Manager for this Flow Z ,
0x19 | 16 | 16 | FlowTarget | UINT32 |  | 168 |  |  | Fz02 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 168 | 0x19_Fz02FlowTarget , DA_Av ,168 ,Av ,168 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x19 | 17 | 17 | FlowMonEnable | Byte |  | 169 |  |  | Fz02 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 169 | 0x19_Fz02FlowMonEnable , DA_Av ,169 ,Av ,169 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x19 | 18 | 18 | MaxPOverflow | UINT16 |  | 170 |  |  | Fz02 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Av | 170 | 0x19_Fz02MaxPOverflow , DA_Av ,170 ,Av ,170 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x19 | 19 | 19 | MaxPUnderflow | UINT16 |  | 171 |  |  | Fz02 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Av | 171 | 0x19_Fz02MaxPUnderflow , DA_Av ,171 ,Av ,171 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x19 | 20 | 20 | FlowSenMap | Byte |  | 172 |  |  | Fz02 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Av | 172 | 0x19_Fz02FlowSenMap , DA_Av ,172 ,Av ,172 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x19 | 21 | 21 | PmvMap | Byte |  | 173 |  |  | Fz02 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Av | 173 | 0x19_Fz02PmvMap , DA_Av ,173 ,Av ,173 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x19 | 22 | 22 | WsAssign | Byte |  | 174 |  |  | Fz02 | Info on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Av | 174 | 0x19_Fz02WsAssign , DA_Av ,174 ,Av ,174 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info on the MainSafe to which this Flow ,
0x19 | 23 | 23 | MonthlyBudget | UINT32 |  | 175 |  |  | Fz02 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Av | 175 | 0x19_Fz02MonthlyBudget , DA_Av ,175 ,Av ,175 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x19 | 24 | 24 | ManualAllowance | UINT16 |  | 176 |  |  | Fz02 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Av | 176 | 0x19_Fz02ManualAllowance , DA_Av ,176 ,Av ,176 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x19 | 25 | 25 | MaxFlowLimit | UINT32 |  | 177 |  |  | Fz02 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Av | 177 | 0x19_Fz02MaxFlowLimit , DA_Av ,177 ,Av ,177 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x19 | 26 | 26 | UnschedFlowLimit | UINT32 |  | 178 |  |  | Fz02 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 178 | 0x19_Fz02UnschedFlowLimit , DA_Av ,178 ,Av ,178 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x19 | 27 | 27 | AlarmSetDelay | UINT16 |  | 179 |  |  | Fz02 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Av | 179 | 0x19_Fz02AlarmSetDelay , DA_Av ,179 ,Av ,179 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x19 | 28 | 28 | AlarmClearDelay | UINT32 |  | 180 |  |  | Fz02 | Time after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Av | 180 | 0x19_Fz02AlarmClearDelay , DA_Av ,180 ,Av ,180 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a Flow Zone alarm is detecte ,
0x19 | 29 | 29 | FlowMgrEnable | Byte |  | 181 |  |  | Fz03 | Enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 181 | 0x19_Fz03FlowMgrEnable , DA_Av ,181 ,Av ,181 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Manager for this Flow Z ,
0x19 | 30 | 30 | FlowTarget | UINT32 |  | 182 |  |  | Fz03 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 182 | 0x19_Fz03FlowTarget , DA_Av ,182 ,Av ,182 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x19 | 31 | 31 | FlowMonEnable | Byte |  | 183 |  |  | Fz03 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 183 | 0x19_Fz03FlowMonEnable , DA_Av ,183 ,Av ,183 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x19 | 32 | 32 | MaxPOverflow | UINT16 |  | 184 |  |  | Fz03 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Av | 184 | 0x19_Fz03MaxPOverflow , DA_Av ,184 ,Av ,184 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x19 | 33 | 33 | MaxPUnderflow | UINT16 |  | 185 |  |  | Fz03 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Av | 185 | 0x19_Fz03MaxPUnderflow , DA_Av ,185 ,Av ,185 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x19 | 34 | 34 | FlowSenMap | Byte |  | 186 |  |  | Fz03 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Av | 186 | 0x19_Fz03FlowSenMap , DA_Av ,186 ,Av ,186 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x19 | 35 | 35 | PmvMap | Byte |  | 187 |  |  | Fz03 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Av | 187 | 0x19_Fz03PmvMap , DA_Av ,187 ,Av ,187 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x19 | 36 | 36 | WsAssign | Byte |  | 188 |  |  | Fz03 | Info on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Av | 188 | 0x19_Fz03WsAssign , DA_Av ,188 ,Av ,188 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info on the MainSafe to which this Flow ,
0x19 | 37 | 37 | MonthlyBudget | UINT32 |  | 189 |  |  | Fz03 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Av | 189 | 0x19_Fz03MonthlyBudget , DA_Av ,189 ,Av ,189 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x19 | 38 | 38 | ManualAllowance | UINT16 |  | 190 |  |  | Fz03 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Av | 190 | 0x19_Fz03ManualAllowance , DA_Av ,190 ,Av ,190 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x19 | 39 | 39 | MaxFlowLimit | UINT32 |  | 191 |  |  | Fz03 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Av | 191 | 0x19_Fz03MaxFlowLimit , DA_Av ,191 ,Av ,191 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x19 | 40 | 40 | UnschedFlowLimit | UINT32 |  | 192 |  |  | Fz03 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 192 | 0x19_Fz03UnschedFlowLimit , DA_Av ,192 ,Av ,192 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x19 | 41 | 41 | AlarmSetDelay | UINT16 |  | 193 |  |  | Fz03 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Av | 193 | 0x19_Fz03AlarmSetDelay , DA_Av ,193 ,Av ,193 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x19 | 42 | 42 | AlarmClearDelay | UINT32 |  | 194 |  |  | Fz03 | Time after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Av | 194 | 0x19_Fz03AlarmClearDelay , DA_Av ,194 ,Av ,194 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a Flow Zone alarm is detecte ,
0x19 | 43 | 43 | FlowMgrEnable | Byte |  | 195 |  |  | Fz04 | Enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 195 | 0x19_Fz04FlowMgrEnable , DA_Av ,195 ,Av ,195 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Manager for this Flow Z ,
0x19 | 44 | 44 | FlowTarget | UINT32 |  | 196 |  |  | Fz04 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 196 | 0x19_Fz04FlowTarget , DA_Av ,196 ,Av ,196 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x19 | 45 | 45 | FlowMonEnable | Byte |  | 197 |  |  | Fz04 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 197 | 0x19_Fz04FlowMonEnable , DA_Av ,197 ,Av ,197 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x19 | 46 | 46 | MaxPOverflow | UINT16 |  | 198 |  |  | Fz04 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Av | 198 | 0x19_Fz04MaxPOverflow , DA_Av ,198 ,Av ,198 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x19 | 47 | 47 | MaxPUnderflow | UINT16 |  | 199 |  |  | Fz04 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Av | 199 | 0x19_Fz04MaxPUnderflow , DA_Av ,199 ,Av ,199 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x19 | 48 | 48 | FlowSenMap | Byte |  | 200 |  |  | Fz04 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Av | 200 | 0x19_Fz04FlowSenMap , DA_Av ,200 ,Av ,200 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x19 | 49 | 49 | PmvMap | Byte |  | 201 |  |  | Fz04 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Av | 201 | 0x19_Fz04PmvMap , DA_Av ,201 ,Av ,201 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x19 | 50 | 50 | WsAssign | Byte |  | 202 |  |  | Fz04 | Info on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Av | 202 | 0x19_Fz04WsAssign , DA_Av ,202 ,Av ,202 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info on the MainSafe to which this Flow ,
0x19 | 51 | 51 | MonthlyBudget | UINT32 |  | 203 |  |  | Fz04 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Av | 203 | 0x19_Fz04MonthlyBudget , DA_Av ,203 ,Av ,203 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x19 | 52 | 52 | ManualAllowance | UINT16 |  | 204 |  |  | Fz04 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Av | 204 | 0x19_Fz04ManualAllowance , DA_Av ,204 ,Av ,204 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x19 | 53 | 53 | MaxFlowLimit | UINT32 |  | 205 |  |  | Fz04 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Av | 205 | 0x19_Fz04MaxFlowLimit , DA_Av ,205 ,Av ,205 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x19 | 54 | 54 | UnschedFlowLimit | UINT32 |  | 206 |  |  | Fz04 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 206 | 0x19_Fz04UnschedFlowLimit , DA_Av ,206 ,Av ,206 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x19 | 55 | 55 | AlarmSetDelay | UINT16 |  | 207 |  |  | Fz04 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Av | 207 | 0x19_Fz04AlarmSetDelay , DA_Av ,207 ,Av ,207 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x19 | 56 | 56 | AlarmClearDelay | UINT32 |  | 208 |  |  | Fz04 | Time after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Av | 208 | 0x19_Fz04AlarmClearDelay , DA_Av ,208 ,Av ,208 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a Flow Zone alarm is detecte ,
0x19 | 57 | 57 | FlowMgrEnable | Byte |  | 209 |  |  | Fz05 | Enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 209 | 0x19_Fz05FlowMgrEnable , DA_Av ,209 ,Av ,209 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Manager for this Flow Z ,
0x19 | 58 | 58 | FlowTarget | UINT32 |  | 210 |  |  | Fz05 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 210 | 0x19_Fz05FlowTarget , DA_Av ,210 ,Av ,210 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x19 | 59 | 59 | FlowMonEnable | Byte |  | 211 |  |  | Fz05 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 211 | 0x19_Fz05FlowMonEnable , DA_Av ,211 ,Av ,211 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x19 | 60 | 60 | MaxPOverflow | UINT16 |  | 212 |  |  | Fz05 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Av | 212 | 0x19_Fz05MaxPOverflow , DA_Av ,212 ,Av ,212 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x19 | 61 | 61 | MaxPUnderflow | UINT16 |  | 213 |  |  | Fz05 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Av | 213 | 0x19_Fz05MaxPUnderflow , DA_Av ,213 ,Av ,213 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x19 | 62 | 62 | FlowSenMap | Byte |  | 214 |  |  | Fz05 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Av | 214 | 0x19_Fz05FlowSenMap , DA_Av ,214 ,Av ,214 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x19 | 63 | 63 | PmvMap | Byte |  | 215 |  |  | Fz05 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Av | 215 | 0x19_Fz05PmvMap , DA_Av ,215 ,Av ,215 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x19 | 64 | 64 | WsAssign | Byte |  | 216 |  |  | Fz05 | Info on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Av | 216 | 0x19_Fz05WsAssign , DA_Av ,216 ,Av ,216 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info on the MainSafe to which this Flow ,
0x19 | 65 | 65 | MonthlyBudget | UINT32 |  | 217 |  |  | Fz05 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Av | 217 | 0x19_Fz05MonthlyBudget , DA_Av ,217 ,Av ,217 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x19 | 66 | 66 | ManualAllowance | UINT16 |  | 218 |  |  | Fz05 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Av | 218 | 0x19_Fz05ManualAllowance , DA_Av ,218 ,Av ,218 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x19 | 67 | 67 | MaxFlowLimit | UINT32 |  | 219 |  |  | Fz05 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Av | 219 | 0x19_Fz05MaxFlowLimit , DA_Av ,219 ,Av ,219 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x19 | 68 | 68 | UnschedFlowLimit | UINT32 |  | 220 |  |  | Fz05 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 220 | 0x19_Fz05UnschedFlowLimit , DA_Av ,220 ,Av ,220 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x19 | 69 | 69 | AlarmSetDelay | UINT16 |  | 221 |  |  | Fz05 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Av | 221 | 0x19_Fz05AlarmSetDelay , DA_Av ,221 ,Av ,221 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x19 | 70 | 70 | AlarmClearDelay | UINT32 |  | 222 |  |  | Fz05 | Time after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Av | 222 | 0x19_Fz05AlarmClearDelay , DA_Av ,222 ,Av ,222 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a Flow Zone alarm is detecte ,
0x19 | 71 | 71 | FlowMgrEnable | Byte |  | 223 |  |  | Fz06 | Enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 223 | 0x19_Fz06FlowMgrEnable , DA_Av ,223 ,Av ,223 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Manager for this Flow Z ,
0x19 | 72 | 72 | FlowTarget | UINT32 |  | 224 |  |  | Fz06 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 224 | 0x19_Fz06FlowTarget , DA_Av ,224 ,Av ,224 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x19 | 73 | 73 | FlowMonEnable | Byte |  | 225 |  |  | Fz06 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Av | 225 | 0x19_Fz06FlowMonEnable , DA_Av ,225 ,Av ,225 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x19 | 74 | 74 | MaxPOverflow | UINT16 |  | 226 |  |  | Fz06 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Av | 226 | 0x19_Fz06MaxPOverflow , DA_Av ,226 ,Av ,226 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x19 | 75 | 75 | MaxPUnderflow | UINT16 |  | 227 |  |  | Fz06 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Av | 227 | 0x19_Fz06MaxPUnderflow , DA_Av ,227 ,Av ,227 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x19 | 76 | 76 | FlowSenMap | Byte |  | 228 |  |  | Fz06 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Av | 228 | 0x19_Fz06FlowSenMap , DA_Av ,228 ,Av ,228 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x19 | 77 | 77 | PmvMap | Byte |  | 229 |  |  | Fz06 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Av | 229 | 0x19_Fz06PmvMap , DA_Av ,229 ,Av ,229 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x19 | 78 | 78 | WsAssign | Byte |  | 230 |  |  | Fz06 | Info on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Av | 230 | 0x19_Fz06WsAssign , DA_Av ,230 ,Av ,230 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info on the MainSafe to which this Flow ,
0x19 | 79 | 79 | MonthlyBudget | UINT32 |  | 231 |  |  | Fz06 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Av | 231 | 0x19_Fz06MonthlyBudget , DA_Av ,231 ,Av ,231 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x19 | 80 | 80 | ManualAllowance | UINT16 |  | 232 |  |  | Fz06 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Av | 232 | 0x19_Fz06ManualAllowance , DA_Av ,232 ,Av ,232 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x19 | 81 | 81 | MaxFlowLimit | UINT32 |  | 233 |  |  | Fz06 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Av | 233 | 0x19_Fz06MaxFlowLimit , DA_Av ,233 ,Av ,233 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x19 | 82 | 82 | UnschedFlowLimit | UINT32 |  | 234 |  |  | Fz06 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Av | 234 | 0x19_Fz06UnschedFlowLimit , DA_Av ,234 ,Av ,234 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x19 | 83 | 83 | AlarmSetDelay | UINT16 |  | 235 |  |  | Fz06 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Av | 235 | 0x19_Fz06AlarmSetDelay , DA_Av ,235 ,Av ,235 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x19 | 84 | 84 | AlarmClearDelay | UINT32 |  | 236 |  |  | Fz06 | Time after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Av | 236 | 0x19_Fz06AlarmClearDelay , DA_Av ,236 ,Av ,236 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time after a Flow Zone alarm is detecte ,
000
0x1A – REPORT FLOW ZONE PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x1A – REPORT FLOW ZONE PARAMETERS
| demo=h19.html | [9 empty] | 000
| Template=Type 1 | [9 empty] | 000
| This command reports all Flow Zone settings for each of the 6 Flow Zones in the controller. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x1A | 0 | 1 | FlowMgrEnable | Byte |  |  |  | 123 | Fz01 | To enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 123 | 0x1A_Fz01FlowMgrEnable , DA_Ai ,123 ,Ai ,123 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,To enable the Flow Manager for this Flo ,
0x1A | 1 | 2 | FlowTarget | UINT32 |  |  |  | 124 | Fz01 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 124 | 0x1A_Fz01FlowTarget , DA_Ai ,124 ,Ai ,124 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x1A | 2 | 3 | FlowMonEnable | Byte |  |  |  | 125 | Fz01 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 125 | 0x1A_Fz01FlowMonEnable , DA_Ai ,125 ,Ai ,125 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x1A | 3 | 4 | MaxPOverflow | UINT16 |  |  |  | 126 | Fz01 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Ai | 126 | 0x1A_Fz01MaxPOverflow , DA_Ai ,126 ,Ai ,126 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x1A | 4 | 5 | MaxPUnderflow | UINT16 |  |  |  | 127 | Fz01 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Ai | 127 | 0x1A_Fz01MaxPUnderflow , DA_Ai ,127 ,Ai ,127 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x1A | 5 | 6 | FlowSenMap | Byte |  |  |  | 128 | Fz01 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Ai | 128 | 0x1A_Fz01FlowSenMap , DA_Ai ,128 ,Ai ,128 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x1A | 6 | 7 | PmvMap | Byte |  |  |  | 129 | Fz01 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Ai | 129 | 0x1A_Fz01PmvMap , DA_Ai ,129 ,Ai ,129 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x1A | 7 | 8 | WsAssign | Byte |  |  |  | 130 | Fz01 | information on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Ai | 130 | 0x1A_Fz01WsAssign , DA_Ai ,130 ,Ai ,130 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,information on the MainSafe to which th ,
0x1A | 8 | 9 | MonthlyBudget | UINT32 |  |  |  | 131 | Fz01 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Ai | 131 | 0x1A_Fz01MonthlyBudget , DA_Ai ,131 ,Ai ,131 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x1A | 9 | 10 | ManualAllowance | UINT16 |  |  |  | 132 | Fz01 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Ai | 132 | 0x1A_Fz01ManualAllowance , DA_Ai ,132 ,Ai ,132 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x1A | 10 | 11 | MaxFlowLimit | UINT32 |  |  |  | 133 | Fz01 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Ai | 133 | 0x1A_Fz01MaxFlowLimit , DA_Ai ,133 ,Ai ,133 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x1A | 11 | 12 | UnschedFlowLimit | UINT32 |  |  |  | 134 | Fz01 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 134 | 0x1A_Fz01UnschedFlowLimit , DA_Ai ,134 ,Ai ,134 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x1A | 12 | 13 | AlarmSetDelay | UINT16 |  |  |  | 135 | Fz01 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Ai | 135 | 0x1A_Fz01AlarmSetDelay , DA_Ai ,135 ,Ai ,135 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x1A | 13 | 14 | AlarmClearDelay | UINT32 |  |  |  | 136 | Fz01 | Tme after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Ai | 136 | 0x1A_Fz01AlarmClearDelay , DA_Ai ,136 ,Ai ,136 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Tme after a Flow Zone alarm is detected ,
0x1A | 14 | 15 | FlowMgrEnable | Byte |  |  |  | 137 | Fz02 | To enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 137 | 0x1A_Fz02FlowMgrEnable , DA_Ai ,137 ,Ai ,137 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,To enable the Flow Manager for this Flo ,
0x1A | 15 | 16 | FlowTarget | UINT32 |  |  |  | 138 | Fz02 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 138 | 0x1A_Fz02FlowTarget , DA_Ai ,138 ,Ai ,138 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x1A | 16 | 17 | FlowMonEnable | Byte |  |  |  | 139 | Fz02 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 139 | 0x1A_Fz02FlowMonEnable , DA_Ai ,139 ,Ai ,139 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x1A | 17 | 18 | MaxPOverflow | UINT16 |  |  |  | 140 | Fz02 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Ai | 140 | 0x1A_Fz02MaxPOverflow , DA_Ai ,140 ,Ai ,140 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x1A | 18 | 19 | MaxPUnderflow | UINT16 |  |  |  | 141 | Fz02 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Ai | 141 | 0x1A_Fz02MaxPUnderflow , DA_Ai ,141 ,Ai ,141 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x1A | 19 | 20 | FlowSenMap | Byte |  |  |  | 142 | Fz02 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Ai | 142 | 0x1A_Fz02FlowSenMap , DA_Ai ,142 ,Ai ,142 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x1A | 20 | 21 | PmvMap | Byte |  |  |  | 143 | Fz02 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Ai | 143 | 0x1A_Fz02PmvMap , DA_Ai ,143 ,Ai ,143 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x1A | 21 | 22 | WsAssign | Byte |  |  |  | 144 | Fz02 | information on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Ai | 144 | 0x1A_Fz02WsAssign , DA_Ai ,144 ,Ai ,144 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,information on the MainSafe to which th ,
0x1A | 22 | 23 | MonthlyBudget | UINT32 |  |  |  | 145 | Fz02 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Ai | 145 | 0x1A_Fz02MonthlyBudget , DA_Ai ,145 ,Ai ,145 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x1A | 23 | 24 | ManualAllowance | UINT16 |  |  |  | 146 | Fz02 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Ai | 146 | 0x1A_Fz02ManualAllowance , DA_Ai ,146 ,Ai ,146 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x1A | 24 | 25 | MaxFlowLimit | UINT32 |  |  |  | 147 | Fz02 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Ai | 147 | 0x1A_Fz02MaxFlowLimit , DA_Ai ,147 ,Ai ,147 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x1A | 25 | 26 | UnschedFlowLimit | UINT32 |  |  |  | 148 | Fz02 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 148 | 0x1A_Fz02UnschedFlowLimit , DA_Ai ,148 ,Ai ,148 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x1A | 26 | 27 | AlarmSetDelay | UINT16 |  |  |  | 149 | Fz02 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Ai | 149 | 0x1A_Fz02AlarmSetDelay , DA_Ai ,149 ,Ai ,149 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x1A | 27 | 28 | AlarmClearDelay | UINT32 |  |  |  | 150 | Fz02 | Tme after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Ai | 150 | 0x1A_Fz02AlarmClearDelay , DA_Ai ,150 ,Ai ,150 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Tme after a Flow Zone alarm is detected ,
0x1A | 28 | 29 | FlowMgrEnable | Byte |  |  |  | 151 | Fz03 | To enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 151 | 0x1A_Fz03FlowMgrEnable , DA_Ai ,151 ,Ai ,151 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,To enable the Flow Manager for this Flo ,
0x1A | 29 | 30 | FlowTarget | UINT32 |  |  |  | 152 | Fz03 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 152 | 0x1A_Fz03FlowTarget , DA_Ai ,152 ,Ai ,152 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x1A | 30 | 31 | FlowMonEnable | Byte |  |  |  | 153 | Fz03 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 153 | 0x1A_Fz03FlowMonEnable , DA_Ai ,153 ,Ai ,153 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x1A | 31 | 32 | MaxPOverflow | UINT16 |  |  |  | 154 | Fz03 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Ai | 154 | 0x1A_Fz03MaxPOverflow , DA_Ai ,154 ,Ai ,154 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x1A | 32 | 33 | MaxPUnderflow | UINT16 |  |  |  | 155 | Fz03 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Ai | 155 | 0x1A_Fz03MaxPUnderflow , DA_Ai ,155 ,Ai ,155 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x1A | 33 | 34 | FlowSenMap | Byte |  |  |  | 156 | Fz03 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Ai | 156 | 0x1A_Fz03FlowSenMap , DA_Ai ,156 ,Ai ,156 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x1A | 34 | 35 | PmvMap | Byte |  |  |  | 157 | Fz03 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Ai | 157 | 0x1A_Fz03PmvMap , DA_Ai ,157 ,Ai ,157 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x1A | 35 | 36 | WsAssign | Byte |  |  |  | 158 | Fz03 | information on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Ai | 158 | 0x1A_Fz03WsAssign , DA_Ai ,158 ,Ai ,158 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,information on the MainSafe to which th ,
0x1A | 36 | 37 | MonthlyBudget | UINT32 |  |  |  | 159 | Fz03 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Ai | 159 | 0x1A_Fz03MonthlyBudget , DA_Ai ,159 ,Ai ,159 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x1A | 37 | 38 | ManualAllowance | UINT16 |  |  |  | 160 | Fz03 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Ai | 160 | 0x1A_Fz03ManualAllowance , DA_Ai ,160 ,Ai ,160 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x1A | 38 | 39 | MaxFlowLimit | UINT32 |  |  |  | 161 | Fz03 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Ai | 161 | 0x1A_Fz03MaxFlowLimit , DA_Ai ,161 ,Ai ,161 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x1A | 39 | 40 | UnschedFlowLimit | UINT32 |  |  |  | 162 | Fz03 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 162 | 0x1A_Fz03UnschedFlowLimit , DA_Ai ,162 ,Ai ,162 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x1A | 40 | 41 | AlarmSetDelay | UINT16 |  |  |  | 163 | Fz03 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Ai | 163 | 0x1A_Fz03AlarmSetDelay , DA_Ai ,163 ,Ai ,163 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x1A | 41 | 42 | AlarmClearDelay | UINT32 |  |  |  | 164 | Fz03 | Tme after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Ai | 164 | 0x1A_Fz03AlarmClearDelay , DA_Ai ,164 ,Ai ,164 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Tme after a Flow Zone alarm is detected ,
0x1A | 42 | 43 | FlowMgrEnable | Byte |  |  |  | 165 | Fz04 | To enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 165 | 0x1A_Fz04FlowMgrEnable , DA_Ai ,165 ,Ai ,165 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,To enable the Flow Manager for this Flo ,
0x1A | 43 | 44 | FlowTarget | UINT32 |  |  |  | 166 | Fz04 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 166 | 0x1A_Fz04FlowTarget , DA_Ai ,166 ,Ai ,166 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x1A | 44 | 45 | FlowMonEnable | Byte |  |  |  | 167 | Fz04 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 167 | 0x1A_Fz04FlowMonEnable , DA_Ai ,167 ,Ai ,167 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x1A | 45 | 46 | MaxPOverflow | UINT16 |  |  |  | 168 | Fz04 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Ai | 168 | 0x1A_Fz04MaxPOverflow , DA_Ai ,168 ,Ai ,168 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x1A | 46 | 47 | MaxPUnderflow | UINT16 |  |  |  | 169 | Fz04 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Ai | 169 | 0x1A_Fz04MaxPUnderflow , DA_Ai ,169 ,Ai ,169 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x1A | 47 | 48 | FlowSenMap | Byte |  |  |  | 170 | Fz04 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Ai | 170 | 0x1A_Fz04FlowSenMap , DA_Ai ,170 ,Ai ,170 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x1A | 48 | 49 | PmvMap | Byte |  |  |  | 171 | Fz04 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Ai | 171 | 0x1A_Fz04PmvMap , DA_Ai ,171 ,Ai ,171 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x1A | 49 | 50 | WsAssign | Byte |  |  |  | 172 | Fz04 | information on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Ai | 172 | 0x1A_Fz04WsAssign , DA_Ai ,172 ,Ai ,172 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,information on the MainSafe to which th ,
0x1A | 50 | 51 | MonthlyBudget | UINT32 |  |  |  | 173 | Fz04 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Ai | 173 | 0x1A_Fz04MonthlyBudget , DA_Ai ,173 ,Ai ,173 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x1A | 51 | 52 | ManualAllowance | UINT16 |  |  |  | 174 | Fz04 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Ai | 174 | 0x1A_Fz04ManualAllowance , DA_Ai ,174 ,Ai ,174 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x1A | 52 | 53 | MaxFlowLimit | UINT32 |  |  |  | 175 | Fz04 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Ai | 175 | 0x1A_Fz04MaxFlowLimit , DA_Ai ,175 ,Ai ,175 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x1A | 53 | 54 | UnschedFlowLimit | UINT32 |  |  |  | 176 | Fz04 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 176 | 0x1A_Fz04UnschedFlowLimit , DA_Ai ,176 ,Ai ,176 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x1A | 54 | 55 | AlarmSetDelay | UINT16 |  |  |  | 177 | Fz04 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Ai | 177 | 0x1A_Fz04AlarmSetDelay , DA_Ai ,177 ,Ai ,177 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x1A | 55 | 56 | AlarmClearDelay | UINT32 |  |  |  | 178 | Fz04 | Tme after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Ai | 178 | 0x1A_Fz04AlarmClearDelay , DA_Ai ,178 ,Ai ,178 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Tme after a Flow Zone alarm is detected ,
0x1A | 56 | 57 | FlowMgrEnable | Byte |  |  |  | 179 | Fz05 | To enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 179 | 0x1A_Fz05FlowMgrEnable , DA_Ai ,179 ,Ai ,179 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,To enable the Flow Manager for this Flo ,
0x1A | 57 | 58 | FlowTarget | UINT32 |  |  |  | 180 | Fz05 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 180 | 0x1A_Fz05FlowTarget , DA_Ai ,180 ,Ai ,180 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x1A | 58 | 59 | FlowMonEnable | Byte |  |  |  | 181 | Fz05 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 181 | 0x1A_Fz05FlowMonEnable , DA_Ai ,181 ,Ai ,181 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x1A | 59 | 60 | MaxPOverflow | UINT16 |  |  |  | 182 | Fz05 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Ai | 182 | 0x1A_Fz05MaxPOverflow , DA_Ai ,182 ,Ai ,182 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x1A | 60 | 61 | MaxPUnderflow | UINT16 |  |  |  | 183 | Fz05 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Ai | 183 | 0x1A_Fz05MaxPUnderflow , DA_Ai ,183 ,Ai ,183 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x1A | 61 | 62 | FlowSenMap | Byte |  |  |  | 184 | Fz05 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Ai | 184 | 0x1A_Fz05FlowSenMap , DA_Ai ,184 ,Ai ,184 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x1A | 62 | 63 | PmvMap | Byte |  |  |  | 185 | Fz05 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Ai | 185 | 0x1A_Fz05PmvMap , DA_Ai ,185 ,Ai ,185 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x1A | 63 | 64 | WsAssign | Byte |  |  |  | 186 | Fz05 | information on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Ai | 186 | 0x1A_Fz05WsAssign , DA_Ai ,186 ,Ai ,186 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,information on the MainSafe to which th ,
0x1A | 64 | 65 | MonthlyBudget | UINT32 |  |  |  | 187 | Fz05 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Ai | 187 | 0x1A_Fz05MonthlyBudget , DA_Ai ,187 ,Ai ,187 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x1A | 65 | 66 | ManualAllowance | UINT16 |  |  |  | 188 | Fz05 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Ai | 188 | 0x1A_Fz05ManualAllowance , DA_Ai ,188 ,Ai ,188 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x1A | 66 | 67 | MaxFlowLimit | UINT32 |  |  |  | 189 | Fz05 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Ai | 189 | 0x1A_Fz05MaxFlowLimit , DA_Ai ,189 ,Ai ,189 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x1A | 67 | 68 | UnschedFlowLimit | UINT32 |  |  |  | 190 | Fz05 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 190 | 0x1A_Fz05UnschedFlowLimit , DA_Ai ,190 ,Ai ,190 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x1A | 68 | 69 | AlarmSetDelay | UINT16 |  |  |  | 191 | Fz05 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Ai | 191 | 0x1A_Fz05AlarmSetDelay , DA_Ai ,191 ,Ai ,191 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x1A | 69 | 70 | AlarmClearDelay | UINT32 |  |  |  | 192 | Fz05 | Tme after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Ai | 192 | 0x1A_Fz05AlarmClearDelay , DA_Ai ,192 ,Ai ,192 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Tme after a Flow Zone alarm is detected ,
0x1A | 70 | 71 | FlowMgrEnable | Byte |  |  |  | 193 | Fz06 | To enable the Flow Manager for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 193 | 0x1A_Fz06FlowMgrEnable , DA_Ai ,193 ,Ai ,193 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,To enable the Flow Manager for this Flo ,
0x1A | 71 | 72 | FlowTarget | UINT32 |  |  |  | 194 | Fz06 | Flow rate target in GPM for this Flow Zone times 10.Ranse is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 194 | 0x1A_Fz06FlowTarget , DA_Ai ,194 ,Ai ,194 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow rate target in GPM for this Flow Z ,
0x1A | 72 | 73 | FlowMonEnable | Byte |  |  |  | 195 | Fz06 | Enable the Flow Monitor for this Flow Zone. 0 – Indicates that the Flow Manager is disabled. 1 – Indicates that the Flow Manager is enabled | 000 | Ai | 195 | 0x1A_Fz06FlowMonEnable , DA_Ai ,195 ,Ai ,195 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable the Flow Monitor for this Flow Z ,
0x1A | 73 | 74 | MaxPOverflow | UINT16 |  |  |  | 196 | Fz06 | Percent overflow before triggering an alarm. Range is 0 & 110 to 300. Defult is 115. | 000 | Ai | 196 | 0x1A_Fz06MaxPOverflow , DA_Ai ,196 ,Ai ,196 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent overflow before triggering an a ,
0x1A | 74 | 75 | MaxPUnderflow | UINT16 |  |  |  | 197 | Fz06 | Percent underflow before triggering an alarm. Range is 0 & 10 to 100. Defult is 50. | 000 | Ai | 197 | 0x1A_Fz06MaxPUnderflow , DA_Ai ,197 ,Ai ,197 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Percent underflow before triggering an ,
0x1A | 75 | 76 | FlowSenMap | Byte |  |  |  | 198 | Fz06 | Bitmap of each flow sensor assigned to the Flow Zone. | 000 | Ai | 198 | 0x1A_Fz06FlowSenMap , DA_Ai ,198 ,Ai ,198 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each flow sensor assigned to ,
0x1A | 76 | 77 | PmvMap | Byte |  |  |  | 199 | Fz06 | Bitmap of each P/MV output assigned to the Flow Zone. | 000 | Ai | 199 | 0x1A_Fz06PmvMap , DA_Ai ,199 ,Ai ,199 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap of each P/MV output assigned to ,
0x1A | 77 | 78 | WsAssign | Byte |  |  |  | 200 | Fz06 | information on the MainSafe to which this Flow Zone is attached. Range is 0 to 6. | 000 | Ai | 200 | 0x1A_Fz06WsAssign , DA_Ai ,200 ,Ai ,200 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,information on the MainSafe to which th ,
0x1A | 78 | 79 | MonthlyBudget | UINT32 |  |  |  | 201 | Fz06 | Monthly water budget for this Flow Zone times 10. Value is in gallons and the range is 0 to 10-000-000.0 in steps of 0.1. | 000 | Ai | 201 | 0x1A_Fz06MonthlyBudget , DA_Ai ,201 ,Ai ,201 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Monthly water budget for this Flow Zone ,
0x1A | 79 | 80 | ManualAllowance | UINT16 |  |  |  | 202 | Fz06 | Manual water (quick couplers- etc.) to allow in addition to controller watering for alarm purposes times 10. Value is GPM. Range is 0 to 6-550.0 in steps of 0.1. | 000 | Ai | 202 | 0x1A_Fz06ManualAllowance , DA_Ai ,202 ,Ai ,202 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Manual water (quick couplers- etc.) to ,
0x1A | 80 | 81 | MaxFlowLimit | UINT32 |  |  |  | 203 | Fz06 | Maximum flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1 | 000 | Ai | 203 | 0x1A_Fz06MaxFlowLimit , DA_Ai ,203 ,Ai ,203 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow limit for this Flow Zone t ,
0x1A | 81 | 82 | UnschedFlowLimit | UINT32 |  |  |  | 204 | Fz06 | Unscheduled flow limit for this Flow Zone times 10. Value is in GPM and the range is 0 to 10-000.0 in steps of 0.1. | 000 | Ai | 204 | 0x1A_Fz06UnschedFlowLimit , DA_Ai ,204 ,Ai ,204 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unscheduled flow limit for this Flow Zo ,
0x1A | 82 | 83 | AlarmSetDelay | UINT16 |  |  |  | 205 | Fz06 | Time that the Flow Zone must be in an alarm condition before setting an alarm. Value is in seconds. Range is 0 to 599 (9L59 m:ss). Default is 120 (2:00 m:ss). | 000 | Ai | 205 | 0x1A_Fz06AlarmSetDelay , DA_Ai ,205 ,Ai ,205 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time that the Flow Zone must be in an a ,
0x1A | 83 | 84 | AlarmClearDelay | UINT32 |  |  |  | 206 | Fz06 | Tme after a Flow Zone alarm is detected before the alarm will automatically be cleared. Value is in seconds. Range is 86-340 (23:59 hh:mm) in 60 second increments. Default is 86-340 (23:59 hh:mm). | 000 | Ai | 206 | 0x1A_Fz06AlarmClearDelay , DA_Ai ,206 ,Ai ,206 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Tme after a Flow Zone alarm is detected ,
000
0x1B – SET FLO+A694W SENSOR PARAMETERS (v2.00.033 and later) | [10 empty] | 000 |  |  |  |  | 0x1B – SET FLO+A694W SENSOR PARAMETERS (v2.00.033 and later)
| demo=h1b.html | [9 empty] | 000
| template=Type1 | [9 empty] | 000
| Sister Service = 0x3b | [9 empty] | 000
| This command sends up to 6 flow sensor parameter settings for the controller. It includes the location, type of sensor installed, and the sensor configuration. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x1B | 0 |  | Trigger_SetFlowSensorParams |  | 11 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 11 | 0x1B_Trigger_SetFlowSensorParams , DA_Bv ,011 ,Bv ,011 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x1B | 1 | 1 | Type | Byte |  | 237 |  |  | FlowSen01 | Type of Flow Sensor being used. | 000 | Av | 237 | 0x1B_FlowSen01Type , DA_Av ,237 ,Av ,237 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x1B | 2 | 2 | Location | Byte |  | 238 |  |  | FlowSen01 | Location of the Sensor. Range is 0 to 1. 0 = Fixed. 1 = Decoder. | 000 | Av | 238 | 0x1B_FlowSen01Location , DA_Av ,238 ,Av ,238 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. Range is 0 to 1 ,
0x1B | 3 | 3 | DecMod | Byte |  | 239 |  |  | FlowSen01 | Decoder Module numb.er respondible for the sensors if location is Decoder Port K. Value is ignored if Location is Fixed. Range is 1 to | 000 | Av | 239 | 0x1B_FlowSen01DecMod , DA_Av ,239 ,Av ,239 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module numb.er respondible for ,
0x1B | 4 | 4 | DecAdd | Byte |  | 240 |  |  | FlowSen01 | Sensor Decoder Address if location is Decoder. Value is ignored if Location is Fized. Range is 1 to 9. | 000 | Av | 240 | 0x1B_FlowSen01DecAdd , DA_Av ,240 ,Av ,240 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address if location is D ,
0x1B | 5 | 5 | Kfactor | UINT32 |  | 241 |  |  | FlowSen01 | K-Factor of the Flow Sensor Times 10-000.Value is ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 represnting actual values of 0.0001 to 999.9999. | 000 | Av | 241 | 0x1B_FlowSen01Kfactor , DA_Av ,241 ,Av ,241 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor Times 10-00 ,
0x1B | 6 | 6 | Offset | UINT32 |  | 242 |  |  | FlowSen01 | Offset of the Flow sensor times 10-000. Value is ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Av | 242 | 0x1B_FlowSen01Offset , DA_Av ,242 ,Av ,242 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x1B | 7 | 7 | PulseRate | UINT32 |  | 243 |  |  | FlowSen01 | Rate per pulse times 10-000 (Fallons or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Av | 243 | 0x1B_FlowSen01PulseRate , DA_Av ,243 ,Av ,243 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Fallons or ,
0x1B | 8 | 8 | PulseUnits | Byte |  | 244 |  |  | FlowSen01 | Units for Pulse Rate. Value is ignored if Type is not Other (Pulses Rate). Range is 0 to 1. 0 = Gallons. 1 = Liters. | 000 | Av | 244 | 0x1B_FlowSen01PulseUnits , DA_Av ,244 ,Av ,244 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units for Pulse Rate. Value is ignored ,
0x1B | 9 | 9 | Wireless | Byte |  | 245 |  |  | FlowSen01 | Flow Sensor is wireless. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless. 1 = Wireless. | 000 | Av | 245 | 0x1B_FlowSen01Wireless , DA_Av ,245 ,Av ,245 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Sensor is wireless. Only applies t ,
0x1B | 10 | 10 | Type | Byte |  | 246 |  |  | FlowSen02 | Type of Flow Sensor being used. | 000 | Av | 246 | 0x1B_FlowSen02Type , DA_Av ,246 ,Av ,246 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x1B | 11 | 11 | Location | Byte |  | 247 |  |  | FlowSen02 | Location of the Sensor. Range is 0 to 1. 0 = Fixed. 1 = Decoder. | 000 | Av | 247 | 0x1B_FlowSen02Location , DA_Av ,247 ,Av ,247 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. Range is 0 to 1 ,
0x1B | 12 | 12 | DecMod | Byte |  | 248 |  |  | FlowSen02 | Decoder Module numb.er respondible for the sensors if location is Decoder Port K. Value is ignored if Location is Fixed. Range is 1 to | 000 | Av | 248 | 0x1B_FlowSen02DecMod , DA_Av ,248 ,Av ,248 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module numb.er respondible for ,
0x1B | 13 | 13 | DecAdd | Byte |  | 249 |  |  | FlowSen02 | Sensor Decoder Address if location is Decoder. Value is ignored if Location is Fized. Range is 1 to 9. | 000 | Av | 249 | 0x1B_FlowSen02DecAdd , DA_Av ,249 ,Av ,249 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address if location is D ,
0x1B | 14 | 14 | Kfactor | UINT32 |  | 250 |  |  | FlowSen02 | K-Factor of the Flow Sensor Times 10-000.Value is ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 represnting actual values of 0.0001 to 999.9999. | 000 | Av | 250 | 0x1B_FlowSen02Kfactor , DA_Av ,250 ,Av ,250 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor Times 10-00 ,
0x1B | 15 | 15 | Offset | UINT32 |  | 251 |  |  | FlowSen02 | Offset of the Flow sensor times 10-000. Value is ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Av | 251 | 0x1B_FlowSen02Offset , DA_Av ,251 ,Av ,251 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x1B | 16 | 16 | PulseRate | UINT32 |  | 252 |  |  | FlowSen02 | Rate per pulse times 10-000 (Fallons or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Av | 252 | 0x1B_FlowSen02PulseRate , DA_Av ,252 ,Av ,252 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Fallons or ,
0x1B | 17 | 17 | PulseUnits | Byte |  | 253 |  |  | FlowSen02 | Units for Pulse Rate. Value is ignored if Type is not Other (Pulses Rate). Range is 0 to 1. 0 = Gallons. 1 = Liters. | 000 | Av | 253 | 0x1B_FlowSen02PulseUnits , DA_Av ,253 ,Av ,253 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units for Pulse Rate. Value is ignored ,
0x1B | 18 | 18 | Wireless | Byte |  | 254 |  |  | FlowSen02 | Flow Sensor is wireless. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless. 1 = Wireless. | 000 | Av | 254 | 0x1B_FlowSen02Wireless , DA_Av ,254 ,Av ,254 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Sensor is wireless. Only applies t ,
0x1B | 19 | 19 | Type | Byte |  | 255 |  |  | FlowSen03 | Type of Flow Sensor being used. | 000 | Av | 255 | 0x1B_FlowSen03Type , DA_Av ,255 ,Av ,255 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x1B | 20 | 20 | Location | Byte |  | 256 |  |  | FlowSen03 | Location of the Sensor. Range is 0 to 1. 0 = Fixed. 1 = Decoder. | 000 | Av | 256 | 0x1B_FlowSen03Location , DA_Av ,256 ,Av ,256 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. Range is 0 to 1 ,
0x1B | 21 | 21 | DecMod | Byte |  | 257 |  |  | FlowSen03 | Decoder Module numb.er respondible for the sensors if location is Decoder Port K. Value is ignored if Location is Fixed. Range is 1 to | 000 | Av | 257 | 0x1B_FlowSen03DecMod , DA_Av ,257 ,Av ,257 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module numb.er respondible for ,
0x1B | 22 | 22 | DecAdd | Byte |  | 258 |  |  | FlowSen03 | Sensor Decoder Address if location is Decoder. Value is ignored if Location is Fized. Range is 1 to 9. | 000 | Av | 258 | 0x1B_FlowSen03DecAdd , DA_Av ,258 ,Av ,258 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address if location is D ,
0x1B | 23 | 23 | Kfactor | UINT32 |  | 259 |  |  | FlowSen03 | K-Factor of the Flow Sensor Times 10-000.Value is ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 represnting actual values of 0.0001 to 999.9999. | 000 | Av | 259 | 0x1B_FlowSen03Kfactor , DA_Av ,259 ,Av ,259 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor Times 10-00 ,
0x1B | 24 | 24 | Offset | UINT32 |  | 260 |  |  | FlowSen03 | Offset of the Flow sensor times 10-000. Value is ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Av | 260 | 0x1B_FlowSen03Offset , DA_Av ,260 ,Av ,260 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x1B | 25 | 25 | PulseRate | UINT32 |  | 261 |  |  | FlowSen03 | Rate per pulse times 10-000 (Fallons or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Av | 261 | 0x1B_FlowSen03PulseRate , DA_Av ,261 ,Av ,261 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Fallons or ,
0x1B | 26 | 26 | PulseUnits | Byte |  | 262 |  |  | FlowSen03 | Units for Pulse Rate. Value is ignored if Type is not Other (Pulses Rate). Range is 0 to 1. 0 = Gallons. 1 = Liters. | 000 | Av | 262 | 0x1B_FlowSen03PulseUnits , DA_Av ,262 ,Av ,262 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units for Pulse Rate. Value is ignored ,
0x1B | 27 | 27 | Wireless | Byte |  | 263 |  |  | FlowSen03 | Flow Sensor is wireless. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless. 1 = Wireless. | 000 | Av | 263 | 0x1B_FlowSen03Wireless , DA_Av ,263 ,Av ,263 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Sensor is wireless. Only applies t ,
0x1B | 28 | 28 | Type | Byte |  | 264 |  |  | FlowSen04 | Type of Flow Sensor being used. | 000 | Av | 264 | 0x1B_FlowSen04Type , DA_Av ,264 ,Av ,264 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x1B | 29 | 29 | Location | Byte |  | 265 |  |  | FlowSen04 | Location of the Sensor. Range is 0 to 1. 0 = Fixed. 1 = Decoder. | 000 | Av | 265 | 0x1B_FlowSen04Location , DA_Av ,265 ,Av ,265 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. Range is 0 to 1 ,
0x1B | 30 | 30 | DecMod | Byte |  | 266 |  |  | FlowSen04 | Decoder Module numb.er respondible for the sensors if location is Decoder Port K. Value is ignored if Location is Fixed. Range is 1 to | 000 | Av | 266 | 0x1B_FlowSen04DecMod , DA_Av ,266 ,Av ,266 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module numb.er respondible for ,
0x1B | 31 | 31 | DecAdd | Byte |  | 267 |  |  | FlowSen04 | Sensor Decoder Address if location is Decoder. Value is ignored if Location is Fized. Range is 1 to 9. | 000 | Av | 267 | 0x1B_FlowSen04DecAdd , DA_Av ,267 ,Av ,267 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address if location is D ,
0x1B | 32 | 32 | Kfactor | UINT32 |  | 268 |  |  | FlowSen04 | K-Factor of the Flow Sensor Times 10-000.Value is ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 represnting actual values of 0.0001 to 999.9999. | 000 | Av | 268 | 0x1B_FlowSen04Kfactor , DA_Av ,268 ,Av ,268 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor Times 10-00 ,
0x1B | 33 | 33 | Offset | UINT32 |  | 269 |  |  | FlowSen04 | Offset of the Flow sensor times 10-000. Value is ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Av | 269 | 0x1B_FlowSen04Offset , DA_Av ,269 ,Av ,269 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x1B | 34 | 34 | PulseRate | UINT32 |  | 270 |  |  | FlowSen04 | Rate per pulse times 10-000 (Fallons or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Av | 270 | 0x1B_FlowSen04PulseRate , DA_Av ,270 ,Av ,270 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Fallons or ,
0x1B | 35 | 35 | PulseUnits | Byte |  | 271 |  |  | FlowSen04 | Units for Pulse Rate. Value is ignored if Type is not Other (Pulses Rate). Range is 0 to 1. 0 = Gallons. 1 = Liters. | 000 | Av | 271 | 0x1B_FlowSen04PulseUnits , DA_Av ,271 ,Av ,271 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units for Pulse Rate. Value is ignored ,
0x1B | 36 | 36 | Wireless | Byte |  | 272 |  |  | FlowSen04 | Flow Sensor is wireless. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless. 1 = Wireless. | 000 | Av | 272 | 0x1B_FlowSen04Wireless , DA_Av ,272 ,Av ,272 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Sensor is wireless. Only applies t ,
0x1B | 37 | 37 | Type | Byte |  | 273 |  |  | FlowSen05 | Type of Flow Sensor being used. | 000 | Av | 273 | 0x1B_FlowSen05Type , DA_Av ,273 ,Av ,273 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x1B | 38 | 38 | Location | Byte |  | 274 |  |  | FlowSen05 | Location of the Sensor. Range is 0 to 1. 0 = Fixed. 1 = Decoder. | 000 | Av | 274 | 0x1B_FlowSen05Location , DA_Av ,274 ,Av ,274 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. Range is 0 to 1 ,
0x1B | 39 | 39 | DecMod | Byte |  | 275 |  |  | FlowSen05 | Decoder Module numb.er respondible for the sensors if location is Decoder Port K. Value is ignored if Location is Fixed. Range is 1 to | 000 | Av | 275 | 0x1B_FlowSen05DecMod , DA_Av ,275 ,Av ,275 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module numb.er respondible for ,
0x1B | 40 | 40 | DecAdd | Byte |  | 276 |  |  | FlowSen05 | Sensor Decoder Address if location is Decoder. Value is ignored if Location is Fized. Range is 1 to 9. | 000 | Av | 276 | 0x1B_FlowSen05DecAdd , DA_Av ,276 ,Av ,276 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address if location is D ,
0x1B | 41 | 41 | Kfactor | UINT32 |  | 277 |  |  | FlowSen05 | K-Factor of the Flow Sensor Times 10-000.Value is ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 represnting actual values of 0.0001 to 999.9999. | 000 | Av | 277 | 0x1B_FlowSen05Kfactor , DA_Av ,277 ,Av ,277 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor Times 10-00 ,
0x1B | 42 | 42 | Offset | UINT32 |  | 278 |  |  | FlowSen05 | Offset of the Flow sensor times 10-000. Value is ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Av | 278 | 0x1B_FlowSen05Offset , DA_Av ,278 ,Av ,278 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x1B | 43 | 43 | PulseRate | UINT32 |  | 279 |  |  | FlowSen05 | Rate per pulse times 10-000 (Fallons or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Av | 279 | 0x1B_FlowSen05PulseRate , DA_Av ,279 ,Av ,279 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Fallons or ,
0x1B | 44 | 44 | PulseUnits | Byte |  | 280 |  |  | FlowSen05 | Units for Pulse Rate. Value is ignored if Type is not Other (Pulses Rate). Range is 0 to 1. 0 = Gallons. 1 = Liters. | 000 | Av | 280 | 0x1B_FlowSen05PulseUnits , DA_Av ,280 ,Av ,280 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units for Pulse Rate. Value is ignored ,
0x1B | 45 | 45 | Wireless | Byte |  | 281 |  |  | FlowSen05 | Flow Sensor is wireless. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless. 1 = Wireless. | 000 | Av | 281 | 0x1B_FlowSen05Wireless , DA_Av ,281 ,Av ,281 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Sensor is wireless. Only applies t ,
0x1B | 46 | 46 | Type | Byte |  | 282 |  |  | FlowSen06 | Type of Flow Sensor being used. | 000 | Av | 282 | 0x1B_FlowSen06Type , DA_Av ,282 ,Av ,282 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x1B | 47 | 47 | Location | Byte |  | 283 |  |  | FlowSen06 | Location of the Sensor. Range is 0 to 1. 0 = Fixed. 1 = Decoder. | 000 | Av | 283 | 0x1B_FlowSen06Location , DA_Av ,283 ,Av ,283 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. Range is 0 to 1 ,
0x1B | 48 | 48 | DecMod | Byte |  | 284 |  |  | FlowSen06 | Decoder Module numb.er respondible for the sensors if location is Decoder Port K. Value is ignored if Location is Fixed. Range is 1 to | 000 | Av | 284 | 0x1B_FlowSen06DecMod , DA_Av ,284 ,Av ,284 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module numb.er respondible for ,
0x1B | 49 | 49 | DecAdd | Byte |  | 285 |  |  | FlowSen06 | Sensor Decoder Address if location is Decoder. Value is ignored if Location is Fized. Range is 1 to 9. | 000 | Av | 285 | 0x1B_FlowSen06DecAdd , DA_Av ,285 ,Av ,285 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address if location is D ,
0x1B | 50 | 50 | Kfactor | UINT32 |  | 286 |  |  | FlowSen06 | K-Factor of the Flow Sensor Times 10-000.Value is ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 represnting actual values of 0.0001 to 999.9999. | 000 | Av | 286 | 0x1B_FlowSen06Kfactor , DA_Av ,286 ,Av ,286 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor Times 10-00 ,
0x1B | 51 | 51 | Offset | UINT32 |  | 287 |  |  | FlowSen06 | Offset of the Flow sensor times 10-000. Value is ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Av | 287 | 0x1B_FlowSen06Offset , DA_Av ,287 ,Av ,287 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x1B | 52 | 52 | PulseRate | UINT32 |  | 288 |  |  | FlowSen06 | Rate per pulse times 10-000 (Fallons or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Av | 288 | 0x1B_FlowSen06PulseRate , DA_Av ,288 ,Av ,288 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Fallons or ,
0x1B | 53 | 53 | PulseUnits | Byte |  | 289 |  |  | FlowSen06 | Units for Pulse Rate. Value is ignored if Type is not Other (Pulses Rate). Range is 0 to 1. 0 = Gallons. 1 = Liters. | 000 | Av | 289 | 0x1B_FlowSen06PulseUnits , DA_Av ,289 ,Av ,289 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units for Pulse Rate. Value is ignored ,
0x1B | 54 | 54 | Wireless | Byte |  | 290 |  |  | FlowSen06 | Flow Sensor is wireless. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless. 1 = Wireless. | 000 | Av | 290 | 0x1B_FlowSen06Wireless , DA_Av ,290 ,Av ,290 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Sensor is wireless. Only applies t ,
000
0x1c– SET CLICK SENSOR PARAMS | [10 empty] | 000 |  |  |  |  | 0x1c– SET CLICK SENSOR PARAMS
| Not implemented | [9 empty] | 000
000
000
0x1D – SET PROGRAM SENSOR ACTION | [10 empty] | 000 |  |  |  |  | 0x1D – SET PROGRAM SENSOR ACTION
| demo=h1d.html | [9 empty] | 000
| template=Type3 | [9 empty] | 000
| sister service = 0x3D | [9 empty] | 000
| This command sets up the Program action for each of the switch type Sensors of the Controller to take when the Sensor is active. Sensors supported include the Clik Sensors and Solar Sync Sensor. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x1D | 0 |  | Trigger _SetPrgmSensorActn |  | 12 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 12 | 0x1D_Trigger _SetPrgmSensorActn , DA_Bv ,012 ,Bv ,012 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x1D | hard Coded = 1 | 1 | Count | Byte |  | 291 |  |  |  | Value indicates the number of Program Sensor action records being sent. Range is 1 to 32. | 000 | Av | 291 | 0x1D_Count , DA_Av ,291 ,Av ,291 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Program S ,
0x1D | 2 | 2 | ProgramNum | Byte |  | 292 |  |  |  | Value indicates the Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Av | 292 | 0x1D_ProgramNum , DA_Av ,292 ,Av ,292 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Program Number for ,
0x1D | 3 | 3 | Clik1Action | Byte |  | 293 |  |  |  | Value idicating the type of action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Av | 293 | 0x1D_Clik1Action , DA_Av ,293 ,Av ,293 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value idicating the type of action to t ,
0x1D | 4 | 4 | Clik2Action | Byte |  | 294 |  |  |  | Value idicating the type of action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Av | 294 | 0x1D_Clik2Action , DA_Av ,294 ,Av ,294 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value idicating the type of action to t ,
0x1D | 5 | 5 | Clik3Action | Byte |  | 295 |  |  |  | Value idicating the type of action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Av | 295 | 0x1D_Clik3Action , DA_Av ,295 ,Av ,295 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value idicating the type of action to t ,
0x1D | 6 | 6 | SSRainAction | Byte |  | 296 |  |  |  | Value indicating the type of action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Av | 296 | 0x1D_SSRainAction , DA_Av ,296 ,Av ,296 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the type of action to ,
0x1D | 7 | 7 | SSFreezeAction | Byte |  | 297 |  |  |  | Value indicating the type of action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Av | 297 | 0x1D_SSFreezeAction , DA_Av ,297 ,Av ,297 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the type of action to ,
000
0x1E – SET FIELD CONTROLLER PROGRAM HEADER DATA (v2.13.000 and Later) | [10 empty] | 000 |  |  |  |  | 0x1E – SET FIELD CONTROLLER PROGRAM HEADER DATA (v2.13.000 and Later)
| demo=h1e.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
| Transmits to a field controller, header data of a specific Field Controller Program. The FCP header is information global to the specified program. It includes various items of a program including the program #, mode, start time(s), schedule, seasonal adjust, no water window times, and event delays. | [9 empty] | 000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x1E | 0 |  | Trigger_SetPrgmHeaderData |  | 13 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 13 | 0x1E_Trigger_SetPrgmHeaderData , DA_Bv ,013 ,Bv ,013 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x1E | 1 | 1 | Program# | Byte |  | 298 |  |  |  | Value indicates the Program Number for which the header data is being sent. Range is 1 to 32. | 000 | Av | 298 | 0x1E_Program# , DA_Av ,298 ,Av ,298 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Program Number for ,
0x1E | 2 | 2 | StackMode | Byte |  | 299 |  |  |  | Value indicates the Stacking Mode for the Program. Range is 0 to 1. 0 = Stack Mode- 1 = Overlap Mode. | 000 | Av | 299 | 0x1E_StackMode , DA_Av ,299 ,Av ,299 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Stacking Mode for t ,
0x1E | 3 | 3 | ScheduleType | Byte |  | 300 |  |  |  | Value indicates the Porgram Type for the Program. Range is 0 to 3. 0 = Day of Week- 1 = Odd/Even- 2 = Interval- 3 = Manual Only | 000 | Av | 300 | 0x1E_ScheduleType , DA_Av ,300 ,Av ,300 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Porgram Type for th ,
0x1E | 4 | 4 | DOWDays | UINT16 |  | 301 |  |  |  | Bitmap indicating the Day of Week Schedule. Indicates days to water (0 = No Water- 1 = Water). Default is all days on. Bits 15-7: Not Used. Bits 6-0: Sunday- Saturday … Monday. | 000 | Av | 301 | 0x1E_DOWDays , DA_Av ,301 ,Av ,301 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap indicating the Day of Week Sched ,
0x1E | 5 | 5 | OddEvenDays | UINT16 |  | 302 |  |  |  | Bitmap indicating the Odd/Even Schedule and No Water Days ( 0 = Water- 1 = No Water). Default is Odd Days- and all No Waters Days all set to zero. | 000 | Av | 302 | 0x1E_OddEvenDays , DA_Av ,302 ,Av ,302 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap indicating the Odd/Even Schedule ,
0x1E | 6 | 6 | IntervalDays | UINT16 |  | 303 |  |  |  | Bitmap indicating the No Water Days (0 = Water- 1 = No Water). Default is all No Water Days set to zero. Bits 15 - 7: Not used. Bits 6-0: Sunday- Saturday … Monday. | 000 | Av | 303 | 0x1E_IntervalDays , DA_Av ,303 ,Av ,303 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap indicating the No Water Days (0 ,
0x1E | 7 | 7 | IntLength | Byte |  | 304 |  |  |  | Byte value indicating the length of the interval schedule. Range is 2 to 31. Default is 2. | 000 | Av | 304 | 0x1E_IntLength , DA_Av ,304 ,Av ,304 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Byte value indicating the length of the ,
0x1E | 8 | 8 | IntNextWater | Byte |  | 305 |  |  |  | Value indicating the number of days before next water day. Range is 0 to 30. Must be at least one less than interval length. Default is 0. | 000 | Av | 305 | 0x1E_IntNextWater , DA_Av ,305 ,Av ,305 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days bef ,
0x1E | 9 | 9 | StartType | Byte |  | 306 |  |  |  | Value indicating the Start Time Type. Range is 0 to 2. 0=Auto- 1 = Start to End- 2 = Manual. | 000 | Av | 306 | 0x1E_StartType , DA_Av ,306 ,Av ,306 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Start Time Type. R ,
0x1E | 10 | 10 | StartTime1 | UINT16 |  | 307 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 307 | 0x1E_StartTime1 , DA_Av ,307 ,Av ,307 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 11 | 11 | StartTime2 | UINT16 |  | 308 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 308 | 0x1E_StartTime2 , DA_Av ,308 ,Av ,308 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 12 | 12 | StartTime3 | UINT16 |  | 309 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 309 | 0x1E_StartTime3 , DA_Av ,309 ,Av ,309 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 13 | 13 | StartTime4 | UINT16 |  | 310 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 310 | 0x1E_StartTime4 , DA_Av ,310 ,Av ,310 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 14 | 14 | StartTime5 | UINT16 |  | 311 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 311 | 0x1E_StartTime5 , DA_Av ,311 ,Av ,311 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 15 | 15 | StartTime6 | UINT16 |  | 312 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 312 | 0x1E_StartTime6 , DA_Av ,312 ,Av ,312 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 16 | 16 | StartTime7 | UINT16 |  | 313 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 313 | 0x1E_StartTime7 , DA_Av ,313 ,Av ,313 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 17 | 17 | StartTime8 | UINT16 |  | 314 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 314 | 0x1E_StartTime8 , DA_Av ,314 ,Av ,314 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 18 | 18 | StartTime9 | UINT16 |  | 315 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 315 | 0x1E_StartTime9 , DA_Av ,315 ,Av ,315 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 19 | 19 | StartTime10 | UINT16 |  | 316 |  |  |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Av | 316 | 0x1E_StartTime10 , DA_Av ,316 ,Av ,316 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x1E | 20 | 20 | SeasAdjSource | Byte |  | 317 |  |  |  | Value indicating the Seasonal Adjust Source to use for the Program. Range in 0 to 3. 0 = Program Seasonal Adjust. 1 = Global Seasonal Adjust. 2 = Global Monthly Seasonal Adjust. 3 = Solar Sync Seasonal Adjust. | 000 | Av | 317 | 0x1E_SeasAdjSource , DA_Av ,317 ,Av ,317 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Seasonal Adjust So ,
0x1E | 21 | 21 | SeasonalAdjust | UINT16 |  | 318 |  |  |  | Value indicating the Program Seasonal Adjust value. Range is 0 to 300. | 000 | Av | 318 | 0x1E_SeasonalAdjust , DA_Av ,318 ,Av ,318 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Program Seasonal A ,
0x1E | 22 | 22 | IgnoreCalDaysOff | Byte |  | 319 |  |  |  | Value indicating whether to ignore any Calendar Days Off for this Program. Range is 0 to 1. 0 = Do not ignore. 1 = Ignore. | 000 | Av | 319 | 0x1E_IgnoreCalDaysOff , DA_Av ,319 ,Av ,319 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether to ignore any ,
0x1E | 23 | 23 | NWWStart | UINT16 |  | 320 |  |  |  | Start time for program No Water Window in Minutes After Midnight. Range is 0 to 1439. Not Used in indicated by FFFFH. | 000 | Av | 320 | 0x1E_NWWStart , DA_Av ,320 ,Av ,320 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Start time for program No Water Window ,
0x1E | 24 | 24 | NWWEnd | UINT16 |  | 321 |  |  |  | End time for program No Water Window in Minutes After Midnight. Range in 0-1439. Not Used is indicated by FFFFH. If not set to Not Used- must be greater or equal to the NWWStart value. | 000 | Av | 321 | 0x1E_NWWEnd , DA_Av ,321 ,Av ,321 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,End time for program No Water Window in ,
0x1E | 25 | 25 | EventDelay | UINT16 |  | 322 |  |  |  | Value indicating the amount of time in seconds to delay between Events. Range is 0 to 21-600 (6 Hours). | 000 | Av | 322 | 0x1E_EventDelay , DA_Av ,322 ,Av ,322 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the amount of time in ,
0x1E | 26 | 26 | STEStartTime | UINT16 |  | 323 |  |  |  | Value indicating the Start to End Start Type Start Time for the program in Minutes After Midnight. Range is 0 - 1439. OFF is indicated by FFFFH. | 000 | Av | 323 | 0x1E_STEStartTime , DA_Av ,323 ,Av ,323 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Start to End Start ,
0x1E | 27 | 27 | STEEndTime | UINT16 |  | 324 |  |  |  | Value indicating the Start to End Start Type Start Time for the program in Minutes After Midnight. Range is 0 - 1439. OFF is indicated by FFFFH. | 000 | Av | 324 | 0x1E_STEEndTime , DA_Av ,324 ,Av ,324 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Start to End Start ,
000
0x1F – SET FIELD CONTROLLER PROGRAM EVENT RUN TIME DATA | [10 empty] | 000 |  |  |  |  | 0x1F – SET FIELD CONTROLLER PROGRAM EVENT RUN TIME DATA
| demo=h1f.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
| Set Event Run Time data for an FCP program, consisting of a Program number, followed by a sequence of Event Types (Stations and/or Blocks) and Run Times. If more Run Times than can fit in a single command are required, multiple commands may be sent in a sequence, as described in the Hunter Command Protocol Structure document. The Events in the command sequence will completely replace the current Events. Only Events with Run Times need to be sent. If an invalid sequence is received, run times will not be altered. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x1F | 0 |  | Trigger_SetPrgmEventRuntime |  | 14 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 14 | 0x1F_Trigger_SetPrgmEventRuntime , DA_Bv ,014 ,Bv ,014 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x1F | 1 | 1 | Sequence | UINT16 |  | 325 |  |  |  | Value contains Sequence Number for this transmission. Range is 0 to 24. Bit 15 will be set on last Sequence. | 000 | Av | 325 | 0x1F_Sequence , DA_Av ,325 ,Av ,325 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains Sequence Number for this ,
0x1F | hardcoded = 1 | 2 | Count | Byte |  | 326 |  |  |  | Value contains the number of events sent in this transmission. Range is 1 – 48. | 000 | Av | 326 | 0x1F_Count , DA_Av ,326 ,Av ,326 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains the number of events sen ,
0x1F | 3 | 3 | ProgramNumber | Byte |  | 327 |  |  |  | Value contains Program Number for which events are being sent. Range is 1 to 32. | 000 | Av | 327 | 0x1F_ProgramNumber , DA_Av ,327 ,Av ,327 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains Program Number for which ,
0x1F | 4 | 4 | EventType | Byte |  | 328 |  |  |  | Value contains the type of Event. Range is 1 to 4. 1 = Station 2 = Block | 000 | Av | 328 | 0x1F_EventType , DA_Av ,328 ,Av ,328 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains the type of Event. Rang ,
0x1F | 5 | 5 | EventID | UINT16 |  | 329 |  |  |  | Value contains the ID of the Event Type being specified. Range is dependent upon Event Type. Station – Range is 1 to 54 for a Conventional Controller and 1 to 225 for a Decoder Controller Block – Range is 1 to 64 Delay – Set to 0 | 000 | Av | 329 | 0x1F_EventID , DA_Av ,329 ,Av ,329 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains the ID of the Event Type ,
0x1F | 6 | 6 | EventRunTime | UINT16 |  | 330 |  |  |  | Value contains Run Time in seconds for the Event. Range is 0 to 43-200 (12 Hours) for a Conventional Station/Block Event or a Delay Event. Range is 0 or 15 to 43-200 (12 Hours) for a Decoder Station/Block Event. | 000 | Av | 330 | 0x1F_EventRunTime , DA_Av ,330 ,Av ,330 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains Run Time in seconds for ,
000
0x20 – SET RAIN DELAY VALUES | [10 empty] | 000 |  |  |  |  | 0x20 – SET RAIN DELAY VALUES
| demo=h20.html | [9 empty] | 000
| Template=Type1 | [9 empty] | 000
| This command will set the rain delay values for all sensors supporting the rain delay feature. Allows an additional number of days to be specified to keep an alarm active after the sensor alarm has cleared. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x20 | 0 |  | Trigger_SetRainDelayValues |  | 15 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 15 | 0x20_Trigger_SetRainDelayValues , DA_Bv ,015 ,Bv ,015 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x20 | 1 | 1 | Clik1Delay | Byte |  | 331 |  |  |  | Value indicating the number of days to keep Clik Sensor X Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Av | 331 | 0x20_Clik1Delay , DA_Av ,331 ,Av ,331 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x20 | 2 | 2 | Clik2Delay | Byte |  | 332 |  |  |  | Value indicating the number of days to keep Clik Sensor X Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Av | 332 | 0x20_Clik2Delay , DA_Av ,332 ,Av ,332 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x20 | 3 | 3 | Clik3Delay | Byte |  | 333 |  |  |  | Value indicating the number of days to keep Clik Sensor X Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Av | 333 | 0x20_Clik3Delay , DA_Av ,333 ,Av ,333 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x20 | 4 | 4 | SSRainDelay | Byte |  | 334 |  |  |  | Value indicating the number of days to keep the Solar Sync Rain Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Av | 334 | 0x20_SSRainDelay , DA_Av ,334 ,Av ,334 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x20 | 5 | 5 | SSFreezeDelay | Byte |  | 335 |  |  |  | Value indicating the number of days to keep the Solar Sync Freeze Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Av | 335 | 0x20_SSFreezeDelay , DA_Av ,335 ,Av ,335 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
000
0x21 – GET RAIN DELAY VALUES | [10 empty] | 000 |  |  |  |  | 0x21 – GET RAIN DELAY VALUES
| demo=h20.html | [9 empty] | 000
| Template=Type1 | [9 empty] | 000
| This command will return the rain delay values for all sensors supporting the rain delay feature. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x21 | 0 | [8 empty] | Write to this point to trigger the action. Value is not important | 000
0x21 | 1 | 1 | Clik1Delay | Byte |  |  |  | 207 |  | Value indicating the number of days to keep Clik Sensor X Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Ai | 207 | 0x21_Clik1Delay , DA_Ai ,207 ,Ai ,207 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x21 | 2 | 2 | Clik2Delay | Byte |  |  |  | 208 |  | Value indicating the number of days to keep Clik Sensor X Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Ai | 208 | 0x21_Clik2Delay , DA_Ai ,208 ,Ai ,208 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x21 | 3 | 3 | Clik3Delay | Byte |  |  |  | 209 |  | Value indicating the number of days to keep Clik Sensor X Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Ai | 209 | 0x21_Clik3Delay , DA_Ai ,209 ,Ai ,209 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x21 | 4 | 4 | SSRainDelay | Byte |  |  |  | 210 |  | Value indicating the number of days to keep the Solar Sync Rain Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Ai | 210 | 0x21_SSRainDelay , DA_Ai ,210 ,Ai ,210 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
0x21 | 5 | 5 | SSFreezeDelay | Byte |  |  |  | 211 |  | Value indicating the number of days to keep the Solar Sync Freeze Alarm active after the sensor alarm has cleared. Range is 0 to 7. | 000 | Ai | 211 | 0x21_SSFreezeDelay , DA_Ai ,211 ,Ai ,211 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days to ,
000
0x23 – SET SEASONAL ADJUST VALUES | [10 empty] | 000 |  |  |  |  | 0x23 – SET SEASONAL ADJUST VALUES
| demo=h23.html | [9 empty] | 000
| Template=Type1 | [9 empty] | 000
| This command wills et the various Seasonal Adjust values for the controller. A signle controller may be addressed for individual control or all controllers coule be address for a blanket change. | [9 empty] | 000
000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x23 | 0 |  | Trigger_SetSeasonalAdjust |  | 16 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 16 | 0x23_Trigger_SetSeasonalAdjust , DA_Bv ,016 ,Bv ,016 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x23 | 1 | 1 | GblSeasAdj | UINT16 |  | 336 |  |  |  | Value of Global Seasonal Adjust Range 0 to 300. | 000 | Av | 336 | 0x23_GblSeasAdj , DA_Av ,336 ,Av ,336 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Global Seasonal Adjust Range 0 ,
0x23 | 2 | 2 | Month1SeasAdj | UINT16 |  | 337 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 337 | 0x23_Month1SeasAdj , DA_Av ,337 ,Av ,337 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 3 | 3 | Month2SeasAdj | UINT16 |  | 338 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 338 | 0x23_Month2SeasAdj , DA_Av ,338 ,Av ,338 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 4 | 4 | Month3SeasAdj | UINT16 |  | 339 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 339 | 0x23_Month3SeasAdj , DA_Av ,339 ,Av ,339 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 5 | 5 | Month4SeasAdj | UINT16 |  | 340 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 340 | 0x23_Month4SeasAdj , DA_Av ,340 ,Av ,340 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 6 | 6 | Month5SeasAdj | UINT16 |  | 341 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 341 | 0x23_Month5SeasAdj , DA_Av ,341 ,Av ,341 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 7 | 7 | Month6SeasAdj | UINT16 |  | 342 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 342 | 0x23_Month6SeasAdj , DA_Av ,342 ,Av ,342 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 8 | 8 | Month7SeasAdj | UINT16 |  | 343 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 343 | 0x23_Month7SeasAdj , DA_Av ,343 ,Av ,343 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 9 | 9 | Month8SeasAdj | UINT16 |  | 344 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 344 | 0x23_Month8SeasAdj , DA_Av ,344 ,Av ,344 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 10 | 10 | Month9SeasAdj | UINT16 |  | 345 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 345 | 0x23_Month9SeasAdj , DA_Av ,345 ,Av ,345 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 11 | 11 | Month10SeasAdj | UINT16 |  | 346 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 346 | 0x23_Month10SeasAdj , DA_Av ,346 ,Av ,346 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 12 | 12 | Month11SeasAdj | UINT16 |  | 347 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 347 | 0x23_Month11SeasAdj , DA_Av ,347 ,Av ,347 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
0x23 | 13 | 13 | Month12SeasAdj | UINT16 |  | 348 |  |  |  | Value of Monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Av | 348 | 0x23_Month12SeasAdj , DA_Av ,348 ,Av ,348 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust values ,
000
000
0x24 – STOP STATIONS | [10 empty] | 000 |  |  |  |  | 0x24 – STOP STATIONS
| demo=h24.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
| This command will allow one or more running stations to be stopped. | [9 empty] | 000
| Extracts the Program number, mode and other params from the Data array and then sends cmd. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x24 | 0 |  | Trigger_StopStations |  | 17 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 17 | 0x24_Trigger_StopStations , DA_Bv ,017 ,Bv ,017 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x24 | hardcoded= 1 | 1 | StaCnt | Byte |  | 349 |  |  |  | Value indicating the number of Stations to stop. Range is 1 to 120. | 000 | Av | 349 | 0x24_StaCnt , DA_Av ,349 ,Av ,349 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of Stations ,
0x24 | 2 | 2 | StationX | UINT16 |  | 350 |  |  |  | Value indicating the Station Number to stop. Range is 1 to. | 000 | Av | 350 | 0x24_StationX , DA_Av ,350 ,Av ,350 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Station Number to ,
000
0x25 – REPORT SEASONAL ADJUST VALUES | [10 empty] | 000 |  |  |  |  | 0x25 – REPORT SEASONAL ADJUST VALUES
| demo=h23.html | [9 empty] | 000
| demo=Type1 | [9 empty] | 000
| This command will return the various Seasonal Adjust values stored in the controller. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x25 | 1 | 1 | GblSeasAdj | UINT16 |  |  |  | 212 |  | Value of Global Seasonal Adjust. Range is 0 to 300. | 000 | Ai | 212 | 0x25_GblSeasAdj , DA_Ai ,212 ,Ai ,212 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Global Seasonal Adjust. Range ,
0x25 | 2 | 2 | Month1SeasAdj | UINT16 |  |  |  | 213 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 213 | 0x25_Month1SeasAdj , DA_Ai ,213 ,Ai ,213 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 3 | 3 | Month2SeasAdj | UINT16 |  |  |  | 214 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 214 | 0x25_Month2SeasAdj , DA_Ai ,214 ,Ai ,214 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 4 | 4 | Month3SeasAdj | UINT16 |  |  |  | 215 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 215 | 0x25_Month3SeasAdj , DA_Ai ,215 ,Ai ,215 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 5 | 5 | Month4SeasAdj | UINT16 |  |  |  | 216 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 216 | 0x25_Month4SeasAdj , DA_Ai ,216 ,Ai ,216 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 6 | 6 | Month5SeasAdj | UINT16 |  |  |  | 217 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 217 | 0x25_Month5SeasAdj , DA_Ai ,217 ,Ai ,217 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 7 | 7 | Month6SeasAdj | UINT16 |  |  |  | 218 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 218 | 0x25_Month6SeasAdj , DA_Ai ,218 ,Ai ,218 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 8 | 8 | Month7SeasAdj | UINT16 |  |  |  | 219 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 219 | 0x25_Month7SeasAdj , DA_Ai ,219 ,Ai ,219 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 9 | 9 | Month8SeasAdj | UINT16 |  |  |  | 220 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 220 | 0x25_Month8SeasAdj , DA_Ai ,220 ,Ai ,220 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 10 | 10 | Month9SeasAdj | UINT16 |  |  |  | 221 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 221 | 0x25_Month9SeasAdj , DA_Ai ,221 ,Ai ,221 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 11 | 11 | Month10SeasAdj | UINT16 |  |  |  | 222 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 222 | 0x25_Month10SeasAdj , DA_Ai ,222 ,Ai ,222 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 12 | 12 | Month11SeasAdj | UINT16 |  |  |  | 223 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 223 | 0x25_Month11SeasAdj , DA_Ai ,223 ,Ai ,223 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
0x25 | 13 | 13 | Month12SeasAdj | UINT16 |  |  |  | 224 |  | Value of Monthly Seasonal Adjust. A total of 12 monthly Seasonal Adjust values will be sent representing January through December. Range 0 to 300. | 000 | Ai | 224 | 0x25_Month12SeasAdj , DA_Ai ,224 ,Ai ,224 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value of Monthly Seasonal Adjust. A to ,
000
0x26 – STOP A PROGRAM | [10 empty] | 000 |  |  |  |  | 0x26 – STOP A PROGRAM
| demo=h26.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
| Transmits to a field controller a command to stop the specified program. Program will be stopped regardless of the irrigation mode in which it is running and any stacked starts will be cleared. | [9 empty] | 000
| Extracts the Program number, mode and other params from the Data array and then sends cmd. | [9 empty] | 000
[10 empty] | Description | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x26 | 0 |  | Trigger_StopPrgm |  | 18 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 18 | 0x26_Trigger_StopPrgm , DA_Bv ,018 ,Bv ,018 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x26 | 1 | 1 | ProgNum | Byte |  | 351 |  |  |  | Value indicating Program Number to stop. Range is 1 to 32. | 000 | Av | 351 | 0x26_ProgNum , DA_Av ,351 ,Av ,351 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating Program Number to stop ,
000
0x27 – DECODER INVENTORY | [10 empty] | 000 |  |  |  |  | 0x27 – DECODER INVENTORY
| Not Implemented | [9 empty] | 000
000
000
0x28 – PURGE LOG RECORDS | [10 empty] | 000 |  |  |  |  | 0x28 – PURGE LOG RECORDS
| demo=h28.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
| This command instructs the controller to adjust its reporting pointers for the specified log based on the log records sent in the last request of command 74H. It indicates that these records were successfully received by the central and they should not be re-sent. The central shall issue this command after every successful reception of reply for command 74H. The use of this command will only affect reporting of log records to the central, not the actual log records. All records are still present in the controller and are viewable via the UI. | [9 empty] | 000
| Extracts the Program number, mode and other params from the Data array and then sends cmd. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x28 | 0 |  | Trigger_PurgeLogs |  | 19 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 19 | 0x28_Trigger_PurgeLogs , DA_Bv ,019 ,Bv ,019 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x28 | LogType | 1 | LogType | Byte |  | 352 |  |  |  | Value indicating the log type for which to purge records. Range is 1 to 3. 1 = Controller Log- 2 = Station Log- 3 = Alarm Log. | 000 | Av | 352 | 0x28_LogType , DA_Av ,352 ,Av ,352 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the log type for which ,
000
0x2B – REPORT FLOW ZONE MONITORING DATA | [10 empty] | 000 |  |  |  |  | 0x2B – REPORT FLOW ZONE MONITORING DATA
| demo=h2b.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports the Flow Monitoring data for each of the 6 Flow Zones in the Controller. Includes information for Flow Zone level monitoring. | [9 empty] | 000
| REJECTED with error 6 | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x2B | 0 | 1 | MonStatus | Byte |  |  |  | 225 | Fz01Data | Value indicates the Flow Zone’s current monitor status. | 000 | Ai | 225 | 0x2B_Fz01DataMonStatus , DA_Ai ,225 ,Ai ,225 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Flow Zone’s current ,
0x2B | 1 | 2 | StaActive | Byte |  |  |  | 226 | Fz01Data | Value indicates whether any Stations are currently active in the Flow Zone. 0 – Stations are not active. 1 – Stations are active. | 000 | Ai | 226 | 0x2B_Fz01DataStaActive , DA_Ai ,226 ,Ai ,226 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 2 | 3 | StaRunning | Byte |  |  |  | 227 | Fz01Data | Value indicates whether any Stations are currently running in the Flow Zone. 0 – Stations are not running. 1 – Stations are running. | 000 | Ai | 227 | 0x2B_Fz01DataStaRunning , DA_Ai ,227 ,Ai ,227 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 3 | 4 | AvgFlow | UINT32 |  |  |  | 228 | Fz01Data | Value indicating the current average flow used for Flow Zone level alarms in GPM * 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 228 | 0x2B_Fz01DataAvgFlow , DA_Ai ,228 ,Ai ,228 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current average fl ,
0x2B | 4 | 5 | AlarmActive | Byte |  |  |  | 229 | Fz01Data | Value indicates whether an alarm is currently active. 0 – Alarm is not active. 1 – Alarm is active. | 000 | Ai | 229 | 0x2B_Fz01DataAlarmActive , DA_Ai ,229 ,Ai ,229 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an alarm is cur ,
0x2B | 5 | 6 | MaxFlowPend | Byte |  |  |  | 230 | Fz01Data | Value indicates whether a maximum flow alarm is pending. 0 – Maximum flow alarm is not pending. 1 – Maximum flow alarm is pending. | 000 | Ai | 230 | 0x2B_Fz01DataMaxFlowPend , DA_Ai ,230 ,Ai ,230 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a maximum flow ,
0x2B | 6 | 7 | UnschedFlowPend | Byte |  |  |  | 231 | Fz01Data | Value indicates whether an unscheduled flow alarm is pending. 0 – Unscheduled flow alarm is not pending. 1 – Unscheduled flow alarm is pending. | 000 | Ai | 231 | 0x2B_Fz01DataUnschedFlowPend , DA_Ai ,231 ,Ai ,231 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an unscheduled ,
0x2B | 7 | 8 | MonStatus | Byte |  |  |  | 232 | Fz02Data | Value indicates the Flow Zone’s current monitor status. | 000 | Ai | 232 | 0x2B_Fz02DataMonStatus , DA_Ai ,232 ,Ai ,232 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Flow Zone’s current ,
0x2B | 8 | 9 | StaActive | Byte |  |  |  | 233 | Fz02Data | Value indicates whether any Stations are currently active in the Flow Zone. 0 – Stations are not active. 1 – Stations are active. | 000 | Ai | 233 | 0x2B_Fz02DataStaActive , DA_Ai ,233 ,Ai ,233 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 9 | 10 | StaRunning | Byte |  |  |  | 234 | Fz02Data | Value indicates whether any Stations are currently running in the Flow Zone. 0 – Stations are not running. 1 – Stations are running. | 000 | Ai | 234 | 0x2B_Fz02DataStaRunning , DA_Ai ,234 ,Ai ,234 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 10 | 11 | AvgFlow | UINT32 |  |  |  | 235 | Fz02Data | Value indicating the current average flow used for Flow Zone level alarms in GPM * 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 235 | 0x2B_Fz02DataAvgFlow , DA_Ai ,235 ,Ai ,235 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current average fl ,
0x2B | 11 | 12 | AlarmActive | Byte |  |  |  | 236 | Fz02Data | Value indicates whether an alarm is currently active. 0 – Alarm is not active. 1 – Alarm is active. | 000 | Ai | 236 | 0x2B_Fz02DataAlarmActive , DA_Ai ,236 ,Ai ,236 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an alarm is cur ,
0x2B | 12 | 13 | MaxFlowPend | Byte |  |  |  | 237 | Fz02Data | Value indicates whether a maximum flow alarm is pending. 0 – Maximum flow alarm is not pending. 1 – Maximum flow alarm is pending. | 000 | Ai | 237 | 0x2B_Fz02DataMaxFlowPend , DA_Ai ,237 ,Ai ,237 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a maximum flow ,
0x2B | 13 | 14 | UnschedFlowPend | Byte |  |  |  | 238 | Fz02Data | Value indicates whether an unscheduled flow alarm is pending. 0 – Unscheduled flow alarm is not pending. 1 – Unscheduled flow alarm is pending. | 000 | Ai | 238 | 0x2B_Fz02DataUnschedFlowPend , DA_Ai ,238 ,Ai ,238 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an unscheduled ,
0x2B | 14 | 15 | MonStatus | Byte |  |  |  | 239 | Fz03Data | Value indicates the Flow Zone’s current monitor status. | 000 | Ai | 239 | 0x2B_Fz03DataMonStatus , DA_Ai ,239 ,Ai ,239 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Flow Zone’s current ,
0x2B | 15 | 16 | StaActive | Byte |  |  |  | 240 | Fz03Data | Value indicates whether any Stations are currently active in the Flow Zone. 0 – Stations are not active. 1 – Stations are active. | 000 | Ai | 240 | 0x2B_Fz03DataStaActive , DA_Ai ,240 ,Ai ,240 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 16 | 17 | StaRunning | Byte |  |  |  | 241 | Fz03Data | Value indicates whether any Stations are currently running in the Flow Zone. 0 – Stations are not running. 1 – Stations are running. | 000 | Ai | 241 | 0x2B_Fz03DataStaRunning , DA_Ai ,241 ,Ai ,241 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 17 | 18 | AvgFlow | UINT32 |  |  |  | 242 | Fz03Data | Value indicating the current average flow used for Flow Zone level alarms in GPM * 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 242 | 0x2B_Fz03DataAvgFlow , DA_Ai ,242 ,Ai ,242 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current average fl ,
0x2B | 18 | 19 | AlarmActive | Byte |  |  |  | 243 | Fz03Data | Value indicates whether an alarm is currently active. 0 – Alarm is not active. 1 – Alarm is active. | 000 | Ai | 243 | 0x2B_Fz03DataAlarmActive , DA_Ai ,243 ,Ai ,243 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an alarm is cur ,
0x2B | 19 | 20 | MaxFlowPend | Byte |  |  |  | 244 | Fz03Data | Value indicates whether a maximum flow alarm is pending. 0 – Maximum flow alarm is not pending. 1 – Maximum flow alarm is pending. | 000 | Ai | 244 | 0x2B_Fz03DataMaxFlowPend , DA_Ai ,244 ,Ai ,244 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a maximum flow ,
0x2B | 20 | 21 | UnschedFlowPend | Byte |  |  |  | 245 | Fz03Data | Value indicates whether an unscheduled flow alarm is pending. 0 – Unscheduled flow alarm is not pending. 1 – Unscheduled flow alarm is pending. | 000 | Ai | 245 | 0x2B_Fz03DataUnschedFlowPend , DA_Ai ,245 ,Ai ,245 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an unscheduled ,
0x2B | 21 | 22 | MonStatus | Byte |  |  |  | 246 | Fz04Data | Value indicates the Flow Zone’s current monitor status. | 000 | Ai | 246 | 0x2B_Fz04DataMonStatus , DA_Ai ,246 ,Ai ,246 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Flow Zone’s current ,
0x2B | 22 | 23 | StaActive | Byte |  |  |  | 247 | Fz04Data | Value indicates whether any Stations are currently active in the Flow Zone. 0 – Stations are not active. 1 – Stations are active. | 000 | Ai | 247 | 0x2B_Fz04DataStaActive , DA_Ai ,247 ,Ai ,247 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 23 | 24 | StaRunning | Byte |  |  |  | 248 | Fz04Data | Value indicates whether any Stations are currently running in the Flow Zone. 0 – Stations are not running. 1 – Stations are running. | 000 | Ai | 248 | 0x2B_Fz04DataStaRunning , DA_Ai ,248 ,Ai ,248 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 24 | 25 | AvgFlow | UINT32 |  |  |  | 249 | Fz04Data | Value indicating the current average flow used for Flow Zone level alarms in GPM * 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 249 | 0x2B_Fz04DataAvgFlow , DA_Ai ,249 ,Ai ,249 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current average fl ,
0x2B | 25 | 26 | AlarmActive | Byte |  |  |  | 250 | Fz04Data | Value indicates whether an alarm is currently active. 0 – Alarm is not active. 1 – Alarm is active. | 000 | Ai | 250 | 0x2B_Fz04DataAlarmActive , DA_Ai ,250 ,Ai ,250 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an alarm is cur ,
0x2B | 26 | 27 | MaxFlowPend | Byte |  |  |  | 251 | Fz04Data | Value indicates whether a maximum flow alarm is pending. 0 – Maximum flow alarm is not pending. 1 – Maximum flow alarm is pending. | 000 | Ai | 251 | 0x2B_Fz04DataMaxFlowPend , DA_Ai ,251 ,Ai ,251 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a maximum flow ,
0x2B | 27 | 28 | UnschedFlowPend | Byte |  |  |  | 252 | Fz04Data | Value indicates whether an unscheduled flow alarm is pending. 0 – Unscheduled flow alarm is not pending. 1 – Unscheduled flow alarm is pending. | 000 | Ai | 252 | 0x2B_Fz04DataUnschedFlowPend , DA_Ai ,252 ,Ai ,252 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an unscheduled ,
0x2B | 28 | 29 | MonStatus | Byte |  |  |  | 253 | Fz05Data | Value indicates the Flow Zone’s current monitor status. | 000 | Ai | 253 | 0x2B_Fz05DataMonStatus , DA_Ai ,253 ,Ai ,253 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Flow Zone’s current ,
0x2B | 29 | 30 | StaActive | Byte |  |  |  | 254 | Fz05Data | Value indicates whether any Stations are currently active in the Flow Zone. 0 – Stations are not active. 1 – Stations are active. | 000 | Ai | 254 | 0x2B_Fz05DataStaActive , DA_Ai ,254 ,Ai ,254 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 30 | 31 | StaRunning | Byte |  |  |  | 255 | Fz05Data | Value indicates whether any Stations are currently running in the Flow Zone. 0 – Stations are not running. 1 – Stations are running. | 000 | Ai | 255 | 0x2B_Fz05DataStaRunning , DA_Ai ,255 ,Ai ,255 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 31 | 32 | AvgFlow | UINT32 |  |  |  | 256 | Fz05Data | Value indicating the current average flow used for Flow Zone level alarms in GPM * 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 256 | 0x2B_Fz05DataAvgFlow , DA_Ai ,256 ,Ai ,256 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current average fl ,
0x2B | 32 | 33 | AlarmActive | Byte |  |  |  | 257 | Fz05Data | Value indicates whether an alarm is currently active. 0 – Alarm is not active. 1 – Alarm is active. | 000 | Ai | 257 | 0x2B_Fz05DataAlarmActive , DA_Ai ,257 ,Ai ,257 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an alarm is cur ,
0x2B | 33 | 34 | MaxFlowPend | Byte |  |  |  | 258 | Fz05Data | Value indicates whether a maximum flow alarm is pending. 0 – Maximum flow alarm is not pending. 1 – Maximum flow alarm is pending. | 000 | Ai | 258 | 0x2B_Fz05DataMaxFlowPend , DA_Ai ,258 ,Ai ,258 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a maximum flow ,
0x2B | 34 | 35 | UnschedFlowPend | Byte |  |  |  | 259 | Fz05Data | Value indicates whether an unscheduled flow alarm is pending. 0 – Unscheduled flow alarm is not pending. 1 – Unscheduled flow alarm is pending. | 000 | Ai | 259 | 0x2B_Fz05DataUnschedFlowPend , DA_Ai ,259 ,Ai ,259 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an unscheduled ,
0x2B | 35 | 36 | MonStatus | Byte |  |  |  | 260 | Fz06Data | Value indicates the Flow Zone’s current monitor status. | 000 | Ai | 260 | 0x2B_Fz06DataMonStatus , DA_Ai ,260 ,Ai ,260 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Flow Zone’s current ,
0x2B | 36 | 37 | StaActive | Byte |  |  |  | 261 | Fz06Data | Value indicates whether any Stations are currently active in the Flow Zone. 0 – Stations are not active. 1 – Stations are active. | 000 | Ai | 261 | 0x2B_Fz06DataStaActive , DA_Ai ,261 ,Ai ,261 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 37 | 38 | StaRunning | Byte |  |  |  | 262 | Fz06Data | Value indicates whether any Stations are currently running in the Flow Zone. 0 – Stations are not running. 1 – Stations are running. | 000 | Ai | 262 | 0x2B_Fz06DataStaRunning , DA_Ai ,262 ,Ai ,262 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether any Stations ar ,
0x2B | 38 | 39 | AvgFlow | UINT32 |  |  |  | 263 | Fz06Data | Value indicating the current average flow used for Flow Zone level alarms in GPM * 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 263 | 0x2B_Fz06DataAvgFlow , DA_Ai ,263 ,Ai ,263 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current average fl ,
0x2B | 39 | 40 | AlarmActive | Byte |  |  |  | 264 | Fz06Data | Value indicates whether an alarm is currently active. 0 – Alarm is not active. 1 – Alarm is active. | 000 | Ai | 264 | 0x2B_Fz06DataAlarmActive , DA_Ai ,264 ,Ai ,264 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an alarm is cur ,
0x2B | 40 | 41 | MaxFlowPend | Byte |  |  |  | 265 | Fz06Data | Value indicates whether a maximum flow alarm is pending. 0 – Maximum flow alarm is not pending. 1 – Maximum flow alarm is pending. | 000 | Ai | 265 | 0x2B_Fz06DataMaxFlowPend , DA_Ai ,265 ,Ai ,265 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether a maximum flow ,
0x2B | 41 | 42 | UnschedFlowPend | Byte |  |  |  | 266 | Fz06Data | Value indicates whether an unscheduled flow alarm is pending. 0 – Unscheduled flow alarm is not pending. 1 – Unscheduled flow alarm is pending. | 000 | Ai | 266 | 0x2B_Fz06DataUnschedFlowPend , DA_Ai ,266 ,Ai ,266 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates whether an unscheduled ,
000
0x2C – REPORT FLOW ZONE DIAGNOSTIC DATA | [10 empty] | 000 |  |  |  |  | 0x2C – REPORT FLOW ZONE DIAGNOSTIC DATA
| demo=h2c.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports the Flow Diagnostic data for each of the 6 Flow Zones in the Controller. Includes information for Station level monitoring. | [9 empty] | 000
| REJECTED with error 6 | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x2C | 0 | 1 | DiagModStatus | Byte |  |  |  | 267 | Fz01Data | Flow Zone’s current monitor status. | 000 | Ai | 267 | 0x2C_Fz01DataDiagModStatus , DA_Ai ,267 ,Ai ,267 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Zone’s current monitor status. ,
0x2C | 1 | 2 | DiadgAvgFlow | UINT32 |  |  |  | 268 | Fz01Data | Current average flow used for Station level diagnostics in GPM times 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 268 | 0x2C_Fz01DataDiadgAvgFlow , DA_Ai ,268 ,Ai ,268 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Station l ,
0x2C | 2 | 3 | DiagExpFlow | UINT32 |  |  |  | 269 | Fz01Data | Expected flow based on the Stations currently runnin gin GPM times 10. | 000 | Ai | 269 | 0x2C_Fz01DataDiagExpFlow , DA_Ai ,269 ,Ai ,269 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Expected flow based on the Stations cur ,
0x2C | 3 | 4 | DiagState | Byte |  |  |  | 270 | Fz01Data | Current state of the Station level diagnostic process. | 000 | Ai | 270 | 0x2C_Fz01DataDiagState , DA_Ai ,270 ,Ai ,270 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current state of the Station level diag ,
0x2C | 4 | 5 | DiagCurSta | UINT16 |  |  |  | 271 | Fz01Data | Current Station being diagnosed. | 000 | Ai | 271 | 0x2C_Fz01DataDiagCurSta , DA_Ai ,271 ,Ai ,271 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current Station being diagnosed. ,
0x2C | 5 | 6 | DiagModStatus | Byte |  |  |  | 272 | Fz02Data | Flow Zone’s current monitor status. | 000 | Ai | 272 | 0x2C_Fz02DataDiagModStatus , DA_Ai ,272 ,Ai ,272 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Zone’s current monitor status. ,
0x2C | 6 | 7 | DiadgAvgFlow | UINT32 |  |  |  | 273 | Fz02Data | Current average flow used for Station level diagnostics in GPM times 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 273 | 0x2C_Fz02DataDiadgAvgFlow , DA_Ai ,273 ,Ai ,273 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Station l ,
0x2C | 7 | 8 | DiagExpFlow | UINT32 |  |  |  | 274 | Fz02Data | Expected flow based on the Stations currently runnin gin GPM times 10. | 000 | Ai | 274 | 0x2C_Fz02DataDiagExpFlow , DA_Ai ,274 ,Ai ,274 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Expected flow based on the Stations cur ,
0x2C | 8 | 9 | DiagState | Byte |  |  |  | 275 | Fz02Data | Current state of the Station level diagnostic process. | 000 | Ai | 275 | 0x2C_Fz02DataDiagState , DA_Ai ,275 ,Ai ,275 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current state of the Station level diag ,
0x2C | 9 | 10 | DiagCurSta | UINT16 |  |  |  | 276 | Fz02Data | Current Station being diagnosed. | 000 | Ai | 276 | 0x2C_Fz02DataDiagCurSta , DA_Ai ,276 ,Ai ,276 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current Station being diagnosed. ,
0x2C | 10 | 11 | DiagModStatus | Byte |  |  |  | 277 | Fz03Data | Flow Zone’s current monitor status. | 000 | Ai | 277 | 0x2C_Fz03DataDiagModStatus , DA_Ai ,277 ,Ai ,277 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Zone’s current monitor status. ,
0x2C | 11 | 12 | DiadgAvgFlow | UINT32 |  |  |  | 278 | Fz03Data | Current average flow used for Station level diagnostics in GPM times 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 278 | 0x2C_Fz03DataDiadgAvgFlow , DA_Ai ,278 ,Ai ,278 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Station l ,
0x2C | 12 | 13 | DiagExpFlow | UINT32 |  |  |  | 279 | Fz03Data | Expected flow based on the Stations currently runnin gin GPM times 10. | 000 | Ai | 279 | 0x2C_Fz03DataDiagExpFlow , DA_Ai ,279 ,Ai ,279 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Expected flow based on the Stations cur ,
0x2C | 13 | 14 | DiagState | Byte |  |  |  | 280 | Fz03Data | Current state of the Station level diagnostic process. | 000 | Ai | 280 | 0x2C_Fz03DataDiagState , DA_Ai ,280 ,Ai ,280 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current state of the Station level diag ,
0x2C | 14 | 15 | DiagCurSta | UINT16 |  |  |  | 281 | Fz03Data | Current Station being diagnosed. | 000 | Ai | 281 | 0x2C_Fz03DataDiagCurSta , DA_Ai ,281 ,Ai ,281 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current Station being diagnosed. ,
0x2C | 15 | 16 | DiagModStatus | Byte |  |  |  | 282 | Fz04Data | Flow Zone’s current monitor status. | 000 | Ai | 282 | 0x2C_Fz04DataDiagModStatus , DA_Ai ,282 ,Ai ,282 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Zone’s current monitor status. ,
0x2C | 16 | 17 | DiadgAvgFlow | UINT32 |  |  |  | 283 | Fz04Data | Current average flow used for Station level diagnostics in GPM times 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 283 | 0x2C_Fz04DataDiadgAvgFlow , DA_Ai ,283 ,Ai ,283 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Station l ,
0x2C | 17 | 18 | DiagExpFlow | UINT32 |  |  |  | 284 | Fz04Data | Expected flow based on the Stations currently runnin gin GPM times 10. | 000 | Ai | 284 | 0x2C_Fz04DataDiagExpFlow , DA_Ai ,284 ,Ai ,284 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Expected flow based on the Stations cur ,
0x2C | 18 | 19 | DiagState | Byte |  |  |  | 285 | Fz04Data | Current state of the Station level diagnostic process. | 000 | Ai | 285 | 0x2C_Fz04DataDiagState , DA_Ai ,285 ,Ai ,285 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current state of the Station level diag ,
0x2C | 19 | 20 | DiagCurSta | UINT16 |  |  |  | 286 | Fz04Data | Current Station being diagnosed. | 000 | Ai | 286 | 0x2C_Fz04DataDiagCurSta , DA_Ai ,286 ,Ai ,286 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current Station being diagnosed. ,
0x2C | 20 | 21 | DiagModStatus | Byte |  |  |  | 287 | Fz05Data | Flow Zone’s current monitor status. | 000 | Ai | 287 | 0x2C_Fz05DataDiagModStatus , DA_Ai ,287 ,Ai ,287 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Zone’s current monitor status. ,
0x2C | 21 | 22 | DiadgAvgFlow | UINT32 |  |  |  | 288 | Fz05Data | Current average flow used for Station level diagnostics in GPM times 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 288 | 0x2C_Fz05DataDiadgAvgFlow , DA_Ai ,288 ,Ai ,288 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Station l ,
0x2C | 22 | 23 | DiagExpFlow | UINT32 |  |  |  | 289 | Fz05Data | Expected flow based on the Stations currently runnin gin GPM times 10. | 000 | Ai | 289 | 0x2C_Fz05DataDiagExpFlow , DA_Ai ,289 ,Ai ,289 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Expected flow based on the Stations cur ,
0x2C | 23 | 24 | DiagState | Byte |  |  |  | 290 | Fz05Data | Current state of the Station level diagnostic process. | 000 | Ai | 290 | 0x2C_Fz05DataDiagState , DA_Ai ,290 ,Ai ,290 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current state of the Station level diag ,
0x2C | 24 | 25 | DiagCurSta | UINT16 |  |  |  | 291 | Fz05Data | Current Station being diagnosed. | 000 | Ai | 291 | 0x2C_Fz05DataDiagCurSta , DA_Ai ,291 ,Ai ,291 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current Station being diagnosed. ,
0x2C | 25 | 26 | DiagModStatus | Byte |  |  |  | 292 | Fz06Data | Flow Zone’s current monitor status. | 000 | Ai | 292 | 0x2C_Fz06DataDiagModStatus , DA_Ai ,292 ,Ai ,292 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Zone’s current monitor status. ,
0x2C | 26 | 27 | DiadgAvgFlow | UINT32 |  |  |  | 293 | Fz06Data | Current average flow used for Station level diagnostics in GPM times 10. A value of 0xFFFFFFFF indicates the average is not yet valid. | 000 | Ai | 293 | 0x2C_Fz06DataDiadgAvgFlow , DA_Ai ,293 ,Ai ,293 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Station l ,
0x2C | 27 | 28 | DiagExpFlow | UINT32 |  |  |  | 294 | Fz06Data | Expected flow based on the Stations currently runnin gin GPM times 10. | 000 | Ai | 294 | 0x2C_Fz06DataDiagExpFlow , DA_Ai ,294 ,Ai ,294 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Expected flow based on the Stations cur ,
0x2C | 28 | 29 | DiagState | Byte |  |  |  | 295 | Fz06Data | Current state of the Station level diagnostic process. | 000 | Ai | 295 | 0x2C_Fz06DataDiagState , DA_Ai ,295 ,Ai ,295 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current state of the Station level diag ,
0x2C | 29 | 30 | DiagCurSta | UINT16 |  |  |  | 296 | Fz06Data | Current Station being diagnosed. | 000 | Ai | 296 | 0x2C_Fz06DataDiagCurSta , DA_Ai ,296 ,Ai ,296 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current Station being diagnosed. ,
000
0x2D – REPORT MAINSAFE MONITORING DATA | [10 empty] | 000 |  |  |  |  | 0x2D – REPORT MAINSAFE MONITORING DATA
| demo=h2d.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports the Flow Monitoring data for each of the 6 MainSafes in the Controller. Includes information for Main Safe level monitoring. | [9 empty] | 000
| REJECTED with error 6 | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x2D | 0 | 1 | MonStatus | Byte |  |  |  | 297 | Fs01Data | Main Safe-s current monitor status. | 000 | Ai | 297 | 0x2D_Fs01DataMonStatus , DA_Ai ,297 ,Ai ,297 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Main Safe-s current monitor status. ,
0x2D | 1 | 2 | StaActive | Byte |  |  |  | 298 | Fs01Data | Any Stations are currently active in the Main Safe. | 000 | Ai | 298 | 0x2D_Fs01DataStaActive , DA_Ai ,298 ,Ai ,298 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any Stations are currently active in th ,
0x2D | 2 | 3 | StaRunning | Byte |  |  |  | 299 | Fs01Data | Any stations are currently running in the Main Safe. | 000 | Ai | 299 | 0x2D_Fs01DataStaRunning , DA_Ai ,299 ,Ai ,299 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any stations are currently running in t ,
0x2D | 3 | 4 | AvgFlow | UINT32 |  |  |  | 300 | Fs01Data | Current average flow used for Main Safe level alarms in GPM * 10. A value of 0xFFFFFFF indicates that average is not yet valid. | 000 | Ai | 300 | 0x2D_Fs01DataAvgFlow , DA_Ai ,300 ,Ai ,300 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Main Safe ,
0x2D | 4 | 5 | AlarmActive | Byte |  |  |  | 301 | Fs01Data | Alarm is currently active. | 000 | Ai | 301 | 0x2D_Fs01DataAlarmActive , DA_Ai ,301 ,Ai ,301 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm is currently active. ,
0x2D | 5 | 6 | MaxFlowPend | Byte |  |  |  | 302 | Fs01Data | Maximum flow alarm is pending- | 000 | Ai | 302 | 0x2D_Fs01DataMaxFlowPend , DA_Ai ,302 ,Ai ,302 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow alarm is pending- ,
0x2D | 6 | 7 | UnschedFlowPend | Byte |  |  |  | 303 | Fs01Data | An unscheduled flow alarm is pending. | 000 | Ai | 303 | 0x2D_Fs01DataUnschedFlowPend , DA_Ai ,303 ,Ai ,303 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,An unscheduled flow alarm is pending. ,
0x2D | 7 | 8 | MonStatus | Byte |  |  |  | 304 | Fs02Data | Main Safe-s current monitor status. | 000 | Ai | 304 | 0x2D_Fs02DataMonStatus , DA_Ai ,304 ,Ai ,304 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Main Safe-s current monitor status. ,
0x2D | 8 | 9 | StaActive | Byte |  |  |  | 305 | Fs02Data | Any Stations are currently active in the Main Safe. | 000 | Ai | 305 | 0x2D_Fs02DataStaActive , DA_Ai ,305 ,Ai ,305 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any Stations are currently active in th ,
0x2D | 9 | 10 | StaRunning | Byte |  |  |  | 306 | Fs02Data | Any stations are currently running in the Main Safe. | 000 | Ai | 306 | 0x2D_Fs02DataStaRunning , DA_Ai ,306 ,Ai ,306 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any stations are currently running in t ,
0x2D | 10 | 11 | AvgFlow | UINT32 |  |  |  | 307 | Fs02Data | Current average flow used for Main Safe level alarms in GPM * 10. A value of 0xFFFFFFF indicates that average is not yet valid. | 000 | Ai | 307 | 0x2D_Fs02DataAvgFlow , DA_Ai ,307 ,Ai ,307 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Main Safe ,
0x2D | 11 | 12 | AlarmActive | Byte |  |  |  | 308 | Fs02Data | Alarm is currently active. | 000 | Ai | 308 | 0x2D_Fs02DataAlarmActive , DA_Ai ,308 ,Ai ,308 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm is currently active. ,
0x2D | 12 | 13 | MaxFlowPend | Byte |  |  |  | 309 | Fs02Data | Maximum flow alarm is pending- | 000 | Ai | 309 | 0x2D_Fs02DataMaxFlowPend , DA_Ai ,309 ,Ai ,309 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow alarm is pending- ,
0x2D | 13 | 14 | UnschedFlowPend | Byte |  |  |  | 310 | Fs02Data | An unscheduled flow alarm is pending. | 000 | Ai | 310 | 0x2D_Fs02DataUnschedFlowPend , DA_Ai ,310 ,Ai ,310 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,An unscheduled flow alarm is pending. ,
0x2D | 14 | 15 | MonStatus | Byte |  |  |  | 311 | Fs03Data | Main Safe-s current monitor status. | 000 | Ai | 311 | 0x2D_Fs03DataMonStatus , DA_Ai ,311 ,Ai ,311 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Main Safe-s current monitor status. ,
0x2D | 15 | 16 | StaActive | Byte |  |  |  | 312 | Fs03Data | Any Stations are currently active in the Main Safe. | 000 | Ai | 312 | 0x2D_Fs03DataStaActive , DA_Ai ,312 ,Ai ,312 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any Stations are currently active in th ,
0x2D | 16 | 17 | StaRunning | Byte |  |  |  | 313 | Fs03Data | Any stations are currently running in the Main Safe. | 000 | Ai | 313 | 0x2D_Fs03DataStaRunning , DA_Ai ,313 ,Ai ,313 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any stations are currently running in t ,
0x2D | 17 | 18 | AvgFlow | UINT32 |  |  |  | 314 | Fs03Data | Current average flow used for Main Safe level alarms in GPM * 10. A value of 0xFFFFFFF indicates that average is not yet valid. | 000 | Ai | 314 | 0x2D_Fs03DataAvgFlow , DA_Ai ,314 ,Ai ,314 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Main Safe ,
0x2D | 18 | 19 | AlarmActive | Byte |  |  |  | 315 | Fs03Data | Alarm is currently active. | 000 | Ai | 315 | 0x2D_Fs03DataAlarmActive , DA_Ai ,315 ,Ai ,315 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm is currently active. ,
0x2D | 19 | 20 | MaxFlowPend | Byte |  |  |  | 316 | Fs03Data | Maximum flow alarm is pending- | 000 | Ai | 316 | 0x2D_Fs03DataMaxFlowPend , DA_Ai ,316 ,Ai ,316 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow alarm is pending- ,
0x2D | 20 | 21 | UnschedFlowPend | Byte |  |  |  | 317 | Fs03Data | An unscheduled flow alarm is pending. | 000 | Ai | 317 | 0x2D_Fs03DataUnschedFlowPend , DA_Ai ,317 ,Ai ,317 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,An unscheduled flow alarm is pending. ,
0x2D | 21 | 22 | MonStatus | Byte |  |  |  | 318 | Fs04Data | Main Safe-s current monitor status. | 000 | Ai | 318 | 0x2D_Fs04DataMonStatus , DA_Ai ,318 ,Ai ,318 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Main Safe-s current monitor status. ,
0x2D | 22 | 23 | StaActive | Byte |  |  |  | 319 | Fs04Data | Any Stations are currently active in the Main Safe. | 000 | Ai | 319 | 0x2D_Fs04DataStaActive , DA_Ai ,319 ,Ai ,319 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any Stations are currently active in th ,
0x2D | 23 | 24 | StaRunning | Byte |  |  |  | 320 | Fs04Data | Any stations are currently running in the Main Safe. | 000 | Ai | 320 | 0x2D_Fs04DataStaRunning , DA_Ai ,320 ,Ai ,320 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any stations are currently running in t ,
0x2D | 24 | 25 | AvgFlow | UINT32 |  |  |  | 321 | Fs04Data | Current average flow used for Main Safe level alarms in GPM * 10. A value of 0xFFFFFFF indicates that average is not yet valid. | 000 | Ai | 321 | 0x2D_Fs04DataAvgFlow , DA_Ai ,321 ,Ai ,321 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Main Safe ,
0x2D | 25 | 26 | AlarmActive | Byte |  |  |  | 322 | Fs04Data | Alarm is currently active. | 000 | Ai | 322 | 0x2D_Fs04DataAlarmActive , DA_Ai ,322 ,Ai ,322 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm is currently active. ,
0x2D | 26 | 27 | MaxFlowPend | Byte |  |  |  | 323 | Fs04Data | Maximum flow alarm is pending- | 000 | Ai | 323 | 0x2D_Fs04DataMaxFlowPend , DA_Ai ,323 ,Ai ,323 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow alarm is pending- ,
0x2D | 27 | 28 | UnschedFlowPend | Byte |  |  |  | 324 | Fs04Data | An unscheduled flow alarm is pending. | 000 | Ai | 324 | 0x2D_Fs04DataUnschedFlowPend , DA_Ai ,324 ,Ai ,324 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,An unscheduled flow alarm is pending. ,
0x2D | 28 | 29 | MonStatus | Byte |  |  |  | 325 | Fs05Data | Main Safe-s current monitor status. | 000 | Ai | 325 | 0x2D_Fs05DataMonStatus , DA_Ai ,325 ,Ai ,325 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Main Safe-s current monitor status. ,
0x2D | 29 | 30 | StaActive | Byte |  |  |  | 326 | Fs05Data | Any Stations are currently active in the Main Safe. | 000 | Ai | 326 | 0x2D_Fs05DataStaActive , DA_Ai ,326 ,Ai ,326 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any Stations are currently active in th ,
0x2D | 30 | 31 | StaRunning | Byte |  |  |  | 327 | Fs05Data | Any stations are currently running in the Main Safe. | 000 | Ai | 327 | 0x2D_Fs05DataStaRunning , DA_Ai ,327 ,Ai ,327 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any stations are currently running in t ,
0x2D | 31 | 32 | AvgFlow | UINT32 |  |  |  | 328 | Fs05Data | Current average flow used for Main Safe level alarms in GPM * 10. A value of 0xFFFFFFF indicates that average is not yet valid. | 000 | Ai | 328 | 0x2D_Fs05DataAvgFlow , DA_Ai ,328 ,Ai ,328 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Main Safe ,
0x2D | 32 | 33 | AlarmActive | Byte |  |  |  | 329 | Fs05Data | Alarm is currently active. | 000 | Ai | 329 | 0x2D_Fs05DataAlarmActive , DA_Ai ,329 ,Ai ,329 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm is currently active. ,
0x2D | 33 | 34 | MaxFlowPend | Byte |  |  |  | 330 | Fs05Data | Maximum flow alarm is pending- | 000 | Ai | 330 | 0x2D_Fs05DataMaxFlowPend , DA_Ai ,330 ,Ai ,330 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow alarm is pending- ,
0x2D | 34 | 35 | UnschedFlowPend | Byte |  |  |  | 331 | Fs05Data | An unscheduled flow alarm is pending. | 000 | Ai | 331 | 0x2D_Fs05DataUnschedFlowPend , DA_Ai ,331 ,Ai ,331 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,An unscheduled flow alarm is pending. ,
0x2D | 35 | 36 | MonStatus | Byte |  |  |  | 332 | Fs06Data | Main Safe-s current monitor status. | 000 | Ai | 332 | 0x2D_Fs06DataMonStatus , DA_Ai ,332 ,Ai ,332 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Main Safe-s current monitor status. ,
0x2D | 36 | 37 | StaActive | Byte |  |  |  | 333 | Fs06Data | Any Stations are currently active in the Main Safe. | 000 | Ai | 333 | 0x2D_Fs06DataStaActive , DA_Ai ,333 ,Ai ,333 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any Stations are currently active in th ,
0x2D | 37 | 38 | StaRunning | Byte |  |  |  | 334 | Fs06Data | Any stations are currently running in the Main Safe. | 000 | Ai | 334 | 0x2D_Fs06DataStaRunning , DA_Ai ,334 ,Ai ,334 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Any stations are currently running in t ,
0x2D | 38 | 39 | AvgFlow | UINT32 |  |  |  | 335 | Fs06Data | Current average flow used for Main Safe level alarms in GPM * 10. A value of 0xFFFFFFF indicates that average is not yet valid. | 000 | Ai | 335 | 0x2D_Fs06DataAvgFlow , DA_Ai ,335 ,Ai ,335 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Current average flow used for Main Safe ,
0x2D | 39 | 40 | AlarmActive | Byte |  |  |  | 336 | Fs06Data | Alarm is currently active. | 000 | Ai | 336 | 0x2D_Fs06DataAlarmActive , DA_Ai ,336 ,Ai ,336 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm is currently active. ,
0x2D | 40 | 41 | MaxFlowPend | Byte |  |  |  | 337 | Fs06Data | Maximum flow alarm is pending- | 000 | Ai | 337 | 0x2D_Fs06DataMaxFlowPend , DA_Ai ,337 ,Ai ,337 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Maximum flow alarm is pending- ,
0x2D | 41 | 42 | UnschedFlowPend | Byte |  |  |  | 338 | Fs06Data | An unscheduled flow alarm is pending. | 000 | Ai | 338 | 0x2D_Fs06DataUnschedFlowPend , DA_Ai ,338 ,Ai ,338 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,An unscheduled flow alarm is pending. ,
000
0x2E – REPORT FLOW MANAGEMENT FLOW DATA | [10 empty] | 000 |  |  |  |  | 0x2E – REPORT FLOW MANAGEMENT FLOW DATA
| demo=h2e.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports the Flow Management flow data for each of the 6 Flow Zones in the Controller. Includes information used by Flow Manager such as the current and target flow. | [9 empty] | 000
| REJECTED with error 6 | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x2E | 0 | 1 | Fz1Flow | UINT32 |  |  |  | 339 |  | Value indicates the current managed flow rate for Flow Zone X times 10. | 000 | Ai | 339 | 0x2E_Fz1Flow , DA_Ai ,339 ,Ai ,339 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the current managed flo ,
0x2E | 1 | 2 | Fz2Flow | UINT32 |  |  |  | 340 |  | Value indicates the current managed flow rate for Flow Zone X times 10. | 000 | Ai | 340 | 0x2E_Fz2Flow , DA_Ai ,340 ,Ai ,340 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the current managed flo ,
0x2E | 2 | 3 | Fz3Flow | UINT32 |  |  |  | 341 |  | Value indicates the current managed flow rate for Flow Zone X times 10. | 000 | Ai | 341 | 0x2E_Fz3Flow , DA_Ai ,341 ,Ai ,341 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the current managed flo ,
0x2E | 3 | 4 | Fz4Flow | UINT32 |  |  |  | 342 |  | Value indicates the current managed flow rate for Flow Zone X times 10. | 000 | Ai | 342 | 0x2E_Fz4Flow , DA_Ai ,342 ,Ai ,342 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the current managed flo ,
0x2E | 4 | 5 | Fz5Flow | UINT32 |  |  |  | 343 |  | Value indicates the current managed flow rate for Flow Zone X times 10. | 000 | Ai | 343 | 0x2E_Fz5Flow , DA_Ai ,343 ,Ai ,343 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the current managed flo ,
0x2E | 5 | 6 | Fz6Flow | UINT32 |  |  |  | 344 |  | Value indicates the current managed flow rate for Flow Zone X times 10. | 000 | Ai | 344 | 0x2E_Fz6Flow , DA_Ai ,344 ,Ai ,344 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the current managed flo ,
0x2E | 6 | 7 | Fz1TgtFlow | UINT32 |  |  |  | 345 |  | Value indicates the target flow rate for Flow Zone X being used by the Flow Manager times 10. | 000 | Ai | 345 | 0x2E_Fz1TgtFlow , DA_Ai ,345 ,Ai ,345 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the target flow rate fo ,
0x2E | 7 | 8 | Fz2TgtFlow | UINT32 |  |  |  | 346 |  | Value indicates the target flow rate for Flow Zone X being used by the Flow Manager times 10. | 000 | Ai | 346 | 0x2E_Fz2TgtFlow , DA_Ai ,346 ,Ai ,346 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the target flow rate fo ,
0x2E | 8 | 9 | Fz3TgtFlow | UINT32 |  |  |  | 347 |  | Value indicates the target flow rate for Flow Zone X being used by the Flow Manager times 10. | 000 | Ai | 347 | 0x2E_Fz3TgtFlow , DA_Ai ,347 ,Ai ,347 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the target flow rate fo ,
0x2E | 9 | 10 | Fz4TgtFlow | UINT32 |  |  |  | 348 |  | Value indicates the target flow rate for Flow Zone X being used by the Flow Manager times 10. | 000 | Ai | 348 | 0x2E_Fz4TgtFlow , DA_Ai ,348 ,Ai ,348 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the target flow rate fo ,
0x2E | 10 | 11 | Fz5TgtFlow | UINT32 |  |  |  | 349 |  | Value indicates the target flow rate for Flow Zone X being used by the Flow Manager times 10. | 000 | Ai | 349 | 0x2E_Fz5TgtFlow , DA_Ai ,349 ,Ai ,349 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the target flow rate fo ,
0x2E | 11 | 12 | Fz6TgtFlow | UINT32 |  |  |  | 350 |  | Value indicates the target flow rate for Flow Zone X being used by the Flow Manager times 10. | 000 | Ai | 350 | 0x2E_Fz6TgtFlow , DA_Ai ,350 ,Ai ,350 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the target flow rate fo ,
000
0x2F – REPORT FLOW MANAGEMENT ACTIVE STATION DATA | [10 empty] | 000 |  |  |  |  | 0x2F – REPORT FLOW MANAGEMENT ACTIVE STATION DATA
| demo=h2f.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports the Flow Management active Station data for the Controller and each of the 32 Programs in the Controller. Includes information used by Flow Manager such as the current and maximum active Stations. | [9 empty] | 000
| REJECTED with error 6 | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x2F | 0 | 1 | FcActSta | Byte |  |  |  | 351 |  | Value indicates the number of Stations currently active for the entire Controller. | 000 | Ai | 351 | 0x2F_FcActSta , DA_Ai ,351 ,Ai ,351 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 1 | 2 | FcMaxActSta | Byte |  |  |  | 352 |  | Value indicates the maximum number of Stations allowed to run simultaneously in the Controller. | 000 | Ai | 352 | 0x2F_FcMaxActSta , DA_Ai ,352 ,Ai ,352 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 2 | 3 | P1ActSta | Byte |  |  |  | 353 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 353 | 0x2F_P1ActSta , DA_Ai ,353 ,Ai ,353 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 3 | 4 | P1MaxActSta | Byte |  |  |  | 354 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 354 | 0x2F_P1MaxActSta , DA_Ai ,354 ,Ai ,354 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 4 | 5 | P2ActSta | Byte |  |  |  | 355 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 355 | 0x2F_P2ActSta , DA_Ai ,355 ,Ai ,355 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 5 | 6 | P2MaxActSta | Byte |  |  |  | 356 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 356 | 0x2F_P2MaxActSta , DA_Ai ,356 ,Ai ,356 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 6 | 7 | P3ActSta | Byte |  |  |  | 357 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 357 | 0x2F_P3ActSta , DA_Ai ,357 ,Ai ,357 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 7 | 8 | P3MaxActSta | Byte |  |  |  | 358 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 358 | 0x2F_P3MaxActSta , DA_Ai ,358 ,Ai ,358 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 8 | 9 | P4ActSta | Byte |  |  |  | 359 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 359 | 0x2F_P4ActSta , DA_Ai ,359 ,Ai ,359 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 9 | 10 | P4MaxActSta | Byte |  |  |  | 360 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 360 | 0x2F_P4MaxActSta , DA_Ai ,360 ,Ai ,360 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 10 | 11 | P5ActSta | Byte |  |  |  | 361 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 361 | 0x2F_P5ActSta , DA_Ai ,361 ,Ai ,361 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 11 | 12 | P5MaxActSta | Byte |  |  |  | 362 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 362 | 0x2F_P5MaxActSta , DA_Ai ,362 ,Ai ,362 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 12 | 13 | P6ActSta | Byte |  |  |  | 363 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 363 | 0x2F_P6ActSta , DA_Ai ,363 ,Ai ,363 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 13 | 14 | P6MaxActSta | Byte |  |  |  | 364 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 364 | 0x2F_P6MaxActSta , DA_Ai ,364 ,Ai ,364 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 14 | 15 | P7ActSta | Byte |  |  |  | 365 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 365 | 0x2F_P7ActSta , DA_Ai ,365 ,Ai ,365 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 15 | 16 | P7MaxActSta | Byte |  |  |  | 366 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 366 | 0x2F_P7MaxActSta , DA_Ai ,366 ,Ai ,366 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 16 | 17 | P8ActSta | Byte |  |  |  | 367 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 367 | 0x2F_P8ActSta , DA_Ai ,367 ,Ai ,367 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 17 | 18 | P8MaxActSta | Byte |  |  |  | 368 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 368 | 0x2F_P8MaxActSta , DA_Ai ,368 ,Ai ,368 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 18 | 19 | P9ActSta | Byte |  |  |  | 369 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 369 | 0x2F_P9ActSta , DA_Ai ,369 ,Ai ,369 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 19 | 20 | P9MaxActSta | Byte |  |  |  | 370 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 370 | 0x2F_P9MaxActSta , DA_Ai ,370 ,Ai ,370 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 20 | 21 | P10ActSta | Byte |  |  |  | 371 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 371 | 0x2F_P10ActSta , DA_Ai ,371 ,Ai ,371 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 21 | 22 | P10MaxActSta | Byte |  |  |  | 372 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 372 | 0x2F_P10MaxActSta , DA_Ai ,372 ,Ai ,372 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 22 | 23 | P11ActSta | Byte |  |  |  | 373 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 373 | 0x2F_P11ActSta , DA_Ai ,373 ,Ai ,373 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 23 | 24 | P11MaxActSta | Byte |  |  |  | 374 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 374 | 0x2F_P11MaxActSta , DA_Ai ,374 ,Ai ,374 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 24 | 25 | P12ActSta | Byte |  |  |  | 375 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 375 | 0x2F_P12ActSta , DA_Ai ,375 ,Ai ,375 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 25 | 26 | P12MaxActSta | Byte |  |  |  | 376 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 376 | 0x2F_P12MaxActSta , DA_Ai ,376 ,Ai ,376 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 26 | 27 | P13ActSta | Byte |  |  |  | 377 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 377 | 0x2F_P13ActSta , DA_Ai ,377 ,Ai ,377 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 27 | 28 | P13MaxActSta | Byte |  |  |  | 378 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 378 | 0x2F_P13MaxActSta , DA_Ai ,378 ,Ai ,378 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 28 | 29 | P14ActSta | Byte |  |  |  | 379 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 379 | 0x2F_P14ActSta , DA_Ai ,379 ,Ai ,379 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 29 | 30 | P14MaxActSta | Byte |  |  |  | 380 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 380 | 0x2F_P14MaxActSta , DA_Ai ,380 ,Ai ,380 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 30 | 31 | P15ActSta | Byte |  |  |  | 381 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 381 | 0x2F_P15ActSta , DA_Ai ,381 ,Ai ,381 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 31 | 32 | P15MaxActSta | Byte |  |  |  | 382 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 382 | 0x2F_P15MaxActSta , DA_Ai ,382 ,Ai ,382 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 32 | 33 | P16ActSta | Byte |  |  |  | 383 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 383 | 0x2F_P16ActSta , DA_Ai ,383 ,Ai ,383 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 33 | 34 | P16MaxActSta | Byte |  |  |  | 384 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 384 | 0x2F_P16MaxActSta , DA_Ai ,384 ,Ai ,384 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 34 | 35 | P17ActSta | Byte |  |  |  | 385 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 385 | 0x2F_P17ActSta , DA_Ai ,385 ,Ai ,385 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 35 | 36 | P17MaxActSta | Byte |  |  |  | 386 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 386 | 0x2F_P17MaxActSta , DA_Ai ,386 ,Ai ,386 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 36 | 37 | P18ActSta | Byte |  |  |  | 387 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 387 | 0x2F_P18ActSta , DA_Ai ,387 ,Ai ,387 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 37 | 38 | P18MaxActSta | Byte |  |  |  | 388 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 388 | 0x2F_P18MaxActSta , DA_Ai ,388 ,Ai ,388 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 38 | 39 | P19ActSta | Byte |  |  |  | 389 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 389 | 0x2F_P19ActSta , DA_Ai ,389 ,Ai ,389 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 39 | 40 | P19MaxActSta | Byte |  |  |  | 390 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 390 | 0x2F_P19MaxActSta , DA_Ai ,390 ,Ai ,390 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 40 | 41 | P20ActSta | Byte |  |  |  | 391 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 391 | 0x2F_P20ActSta , DA_Ai ,391 ,Ai ,391 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 41 | 42 | P20MaxActSta | Byte |  |  |  | 392 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 392 | 0x2F_P20MaxActSta , DA_Ai ,392 ,Ai ,392 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 42 | 43 | P21ActSta | Byte |  |  |  | 393 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 393 | 0x2F_P21ActSta , DA_Ai ,393 ,Ai ,393 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 43 | 44 | P21MaxActSta | Byte |  |  |  | 394 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 394 | 0x2F_P21MaxActSta , DA_Ai ,394 ,Ai ,394 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 44 | 45 | P22ActSta | Byte |  |  |  | 395 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 395 | 0x2F_P22ActSta , DA_Ai ,395 ,Ai ,395 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 45 | 46 | P22MaxActSta | Byte |  |  |  | 396 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 396 | 0x2F_P22MaxActSta , DA_Ai ,396 ,Ai ,396 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 46 | 47 | P23ActSta | Byte |  |  |  | 397 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 397 | 0x2F_P23ActSta , DA_Ai ,397 ,Ai ,397 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 47 | 48 | P23MaxActSta | Byte |  |  |  | 398 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 398 | 0x2F_P23MaxActSta , DA_Ai ,398 ,Ai ,398 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 48 | 49 | P24ActSta | Byte |  |  |  | 399 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 399 | 0x2F_P24ActSta , DA_Ai ,399 ,Ai ,399 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 49 | 50 | P24MaxActSta | Byte |  |  |  | 400 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 400 | 0x2F_P24MaxActSta , DA_Ai ,400 ,Ai ,400 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 50 | 51 | P25ActSta | Byte |  |  |  | 401 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 401 | 0x2F_P25ActSta , DA_Ai ,401 ,Ai ,401 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 51 | 52 | P25MaxActSta | Byte |  |  |  | 402 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 402 | 0x2F_P25MaxActSta , DA_Ai ,402 ,Ai ,402 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 52 | 53 | P26ActSta | Byte |  |  |  | 403 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 403 | 0x2F_P26ActSta , DA_Ai ,403 ,Ai ,403 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 53 | 54 | P26MaxActSta | Byte |  |  |  | 404 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 404 | 0x2F_P26MaxActSta , DA_Ai ,404 ,Ai ,404 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 54 | 55 | P27ActSta | Byte |  |  |  | 405 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 405 | 0x2F_P27ActSta , DA_Ai ,405 ,Ai ,405 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 55 | 56 | P27MaxActSta | Byte |  |  |  | 406 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 406 | 0x2F_P27MaxActSta , DA_Ai ,406 ,Ai ,406 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 56 | 57 | P28ActSta | Byte |  |  |  | 407 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 407 | 0x2F_P28ActSta , DA_Ai ,407 ,Ai ,407 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 57 | 58 | P28MaxActSta | Byte |  |  |  | 408 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 408 | 0x2F_P28MaxActSta , DA_Ai ,408 ,Ai ,408 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 58 | 59 | P29ActSta | Byte |  |  |  | 409 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 409 | 0x2F_P29ActSta , DA_Ai ,409 ,Ai ,409 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 59 | 60 | P29MaxActSta | Byte |  |  |  | 410 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 410 | 0x2F_P29MaxActSta , DA_Ai ,410 ,Ai ,410 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 60 | 61 | P30ActSta | Byte |  |  |  | 411 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 411 | 0x2F_P30ActSta , DA_Ai ,411 ,Ai ,411 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 61 | 62 | P30MaxActSta | Byte |  |  |  | 412 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 412 | 0x2F_P30MaxActSta , DA_Ai ,412 ,Ai ,412 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 62 | 63 | P31ActSta | Byte |  |  |  | 413 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 413 | 0x2F_P31ActSta , DA_Ai ,413 ,Ai ,413 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 63 | 64 | P31MaxActSta | Byte |  |  |  | 414 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 414 | 0x2F_P31MaxActSta , DA_Ai ,414 ,Ai ,414 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
0x2F | 64 | 65 | P32ActSta | Byte |  |  |  | 415 |  | Value indicates the number of Stations currently active for Program X. | 000 | Ai | 415 | 0x2F_P32ActSta , DA_Ai ,415 ,Ai ,415 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the number of Stations ,
0x2F | 65 | 66 | P32MaxActSta | Byte |  |  |  | 416 |  | Value indicates the maximum number of Stations allowed to run simultaneously in Program X. | 000 | Ai | 416 | 0x2F_P32MaxActSta , DA_Ai ,416 ,Ai ,416 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the maximum number of S ,
000
0x30 – REPORT CONTROLLER CURRENT DRAWS (v2.00.016 and later) | [10 empty] | 000 |  |  |  |  | 0x30 – REPORT CONTROLLER CURRENT DRAWS (v2.00.016 and later)
| demo=h30.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports all high-level current draw information available in the Controller to the Central. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x30 | 0 | 1 | XfmrCurDraw | UINT16 |  |  |  | 417 |  | Value indicating the current draw in mA for the transformer. Range is 0 to 65-535mA. | 000 | Ai | 417 | 0x30_XfmrCurDraw , DA_Ai ,417 ,Ai ,417 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current draw in mA ,
0x30 | 1 | 2 | DecMod1Current | UINT16 |  |  |  | 418 |  | Value indicating the current draw for Decoder Module X in mA. Range is 0 to 3200mA- and 0xFFFF. A value of 0xFFFF indicates that the module is not present in inventory or this is a conventional Controller. | 000 | Ai | 418 | 0x30_DecMod1Current , DA_Ai ,418 ,Ai ,418 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current draw for D ,
0x30 | 2 | 3 | DecMod2Current | UINT16 |  |  |  | 419 |  | Value indicating the current draw for Decoder Module X in mA. Range is 0 to 3200mA- and 0xFFFF. A value of 0xFFFF indicates that the module is not present in inventory or this is a conventional Controller. | 000 | Ai | 419 | 0x30_DecMod2Current , DA_Ai ,419 ,Ai ,419 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current draw for D ,
0x30 | 3 | 4 | DecMod3Current | UINT16 |  |  |  | 420 |  | Value indicating the current draw for Decoder Module X in mA. Range is 0 to 3200mA- and 0xFFFF. A value of 0xFFFF indicates that the module is not present in inventory or this is a conventional Controller. | 000 | Ai | 420 | 0x30_DecMod3Current , DA_Ai ,420 ,Ai ,420 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current draw for D ,
000
0x32 – REPORT ITEM NAMES (v.2.00.016 and later) | [10 empty] | 000 |  |  |  |  | 0x32 – REPORT ITEM NAMES (v.2.00.016 and later)
| Web page needed - Itemnames[1..25] | [9 empty] | 000
| This command reports Item Names for the specified Item Type. Multiple Item Names may be returned in the command and will be in order starting at the specified Item Number. Item Names will only be sent up to their terminating character to allow the maximum number of names to be sent in a single transmission. Depending on the Item Type and the length of the Item Names, multiple transmissions may be required to retrieve all the Item Names. The starting Item Number is sent in the request for this purpose. If a request is made and the last Item Number received is less than the maximum number of the specified Item Type stored in the controller, then additional request(s) will be required. This process will repeat until Item Names for the Item Type are reported. | [9 empty] | 000
| Only one item gets stored. When multiple items are returned we discard excess data | [9 empty] | 000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x32 | 0 |  | Trigge_ReportItemNames |  | 20 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 20 | 0x32_Trigge_ReportItemNames , DA_Bv ,020 ,Bv ,020 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x32 | 1 | 1 | ItemType | Byte |  | 353 |  |  |  | Value is the Item Type for which the name is being sent. Range is 1 to 6. 1 = Station Name- 2 = Block Name- 3 = Program Name- 4 = Clik Sensor- 5 = MainSafe- 6 = Flow Zone | 000 | Av | 353 | 0x32_ItemType , DA_Av ,353 ,Av ,353 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value is the Item Type for which the na ,
0x32 | 2 | 2 | StartItemNumber | UINT16 |  | 354 |  |  |  | Value is the Item Number of the Item Type for which to start sending names. Indicates Station Number- Program Number- etc. Range is Dependent on Item Type. Station Number = 1 to 225- Block Number = 1 to 64- Program Number = 1 to 32- Clik Sensor = 1 to 3- MainSafe = 1 to 6- Flow Zone = 1 to 6 | 000 | Av | 354 | 0x32_StartItemNumber , DA_Av ,354 ,Av ,354 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value is the Item Number of the Item Ty ,
0x32 | [10 empty] | 000
0x32 | 3 | 3 | Count | Byte |  |  |  | 421 |  | Contains the number of Item Names sent in this transmission. Range is 1 to 63 | 000 | Ai | 421 | 0x32_Count , DA_Ai ,421 ,Ai ,421 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the number of Item Names sent ,
0x32 | 4 | 4 | ItemType | Byte |  |  |  | 422 |  | Value is the Item Type for which the name is being sent. Range is 1 to 6. 1 = Station Name- 2 = Block Name- 3 = Program Name- 4 = Clik Sensor- 5 = MainSafe- 6 = Flow Zone | 000 | Ai | 422 | 0x32_ItemType , DA_Ai ,422 ,Ai ,422 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value is the Item Type for which the na ,
0x32 | 5 | 5 | ItemNumber | UINT16 |  |  |  | 423 |  | Value is the Item Number of the Item Type for which the name is being sent. Indicates Station Number- Program Number- etc. Range is Dependent on Item Type. Station Number = 1 to 225- Block Number = 1 to 64- Program Number = 1 to 32- Clik Sensor = 1 to 3- MainSafe = 1 to 6- Flow Zone = 1 to 6 | 000 | Ai | 423 | 0x32_ItemNumber , DA_Ai ,423 ,Ai ,423 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value is the Item Number of the Item Ty ,
0x32 | 6 | 6 | ItemName[0] | Byte |  |  |  | 424 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 424 | 0x32_ItemName[0] , DA_Ai ,424 ,Ai ,424 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 7 | 7 | ItemName[1] | Byte |  |  |  | 425 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 425 | 0x32_ItemName[1] , DA_Ai ,425 ,Ai ,425 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 8 | 8 | ItemName[2] | Byte |  |  |  | 426 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 426 | 0x32_ItemName[2] , DA_Ai ,426 ,Ai ,426 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 9 | 9 | ItemName[3] | Byte |  |  |  | 427 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 427 | 0x32_ItemName[3] , DA_Ai ,427 ,Ai ,427 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 10 | 10 | ItemName[4] | Byte |  |  |  | 428 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 428 | 0x32_ItemName[4] , DA_Ai ,428 ,Ai ,428 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 11 | 11 | ItemName[5] | Byte |  |  |  | 429 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 429 | 0x32_ItemName[5] , DA_Ai ,429 ,Ai ,429 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 12 | 12 | ItemName[6] | Byte |  |  |  | 430 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 430 | 0x32_ItemName[6] , DA_Ai ,430 ,Ai ,430 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 13 | 13 | ItemName[7] | Byte |  |  |  | 431 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 431 | 0x32_ItemName[7] , DA_Ai ,431 ,Ai ,431 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 14 | 14 | ItemName[8] | Byte |  |  |  | 432 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 432 | 0x32_ItemName[8] , DA_Ai ,432 ,Ai ,432 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 15 | 15 | ItemName[9] | Byte |  |  |  | 433 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 433 | 0x32_ItemName[9] , DA_Ai ,433 ,Ai ,433 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 16 | 16 | ItemName[10] | Byte |  |  |  | 434 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 434 | 0x32_ItemName[10] , DA_Ai ,434 ,Ai ,434 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 17 | 17 | ItemName[11] | Byte |  |  |  | 435 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 435 | 0x32_ItemName[11] , DA_Ai ,435 ,Ai ,435 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 18 | 18 | ItemName[12] | Byte |  |  |  | 436 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 436 | 0x32_ItemName[12] , DA_Ai ,436 ,Ai ,436 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 19 | 19 | ItemName[13] | Byte |  |  |  | 437 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 437 | 0x32_ItemName[13] , DA_Ai ,437 ,Ai ,437 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 20 | 20 | ItemName[14] | Byte |  |  |  | 438 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 438 | 0x32_ItemName[14] , DA_Ai ,438 ,Ai ,438 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 21 | 21 | ItemName[15] | Byte |  |  |  | 439 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 439 | 0x32_ItemName[15] , DA_Ai ,439 ,Ai ,439 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 22 | 22 | ItemName[16] | Byte |  |  |  | 440 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 440 | 0x32_ItemName[16] , DA_Ai ,440 ,Ai ,440 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 23 | 23 | ItemName[17] | Byte |  |  |  | 441 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 441 | 0x32_ItemName[17] , DA_Ai ,441 ,Ai ,441 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 24 | 24 | ItemName[18] | Byte |  |  |  | 442 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 442 | 0x32_ItemName[18] , DA_Ai ,442 ,Ai ,442 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 25 | 25 | ItemName[19] | Byte |  |  |  | 443 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 443 | 0x32_ItemName[19] , DA_Ai ,443 ,Ai ,443 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 26 | 26 | ItemName[20] | Byte |  |  |  | 444 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 444 | 0x32_ItemName[20] , DA_Ai ,444 ,Ai ,444 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 27 | 27 | ItemName[21] | Byte |  |  |  | 445 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 445 | 0x32_ItemName[21] , DA_Ai ,445 ,Ai ,445 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 28 | 28 | ItemName[22] | Byte |  |  |  | 446 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 446 | 0x32_ItemName[22] , DA_Ai ,446 ,Ai ,446 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 29 | 29 | ItemName[23] | Byte |  |  |  | 447 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 447 | 0x32_ItemName[23] , DA_Ai ,447 ,Ai ,447 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 30 | 30 | ItemName[24] | Byte |  |  |  | 448 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 448 | 0x32_ItemName[24] , DA_Ai ,448 ,Ai ,448 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
0x32 | 31 | 31 | ItemName[25] | Byte |  |  |  | 449 |  | Name of specified Item. The name consists of a maximum of 25 characters encoded in UTF-8 Unicode. Length is variable up to a maximum of 40 bytes plus a NULL terminator so multi-byte Unicode characters can be used. A NULL value of 0 is used to indicate the end of the Item Name. | 000 | Ai | 449 | 0x32_ItemName[25] , DA_Ai ,449 ,Ai ,449 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Name of specified Item. The name consis ,
000
000
0x33 – REPORT STATION PARAMETERS (v.2.00.016 and later) | [10 empty] | 000 |  |  |  |  | 0x33 – REPORT STATION PARAMETERS (v.2.00.016 and later)
000
000
| Partner service : | 0x13 – SET STATION PARAMETERS | [8 empty] | 000
| This command reports all station level parameters stored in the controller back to the central starting at the specified station. Depending on the size of the controller, multiple requests of this command may be required to retrieve all the stations since only 18 of up to 225 stations fit in a single transmission. The starting station number is sent in the request for this purpose. If a request is made and 18 stations are returned, then an additional request will be required. This process will repeat until less than 18 stations are reported. | [9 empty] | 000
| REJECTED with error 251 | [9 empty] | 000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x33 | 0 |  | Trigger_ReportStnParams |  | 21 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 21 | 0x33_Trigger_ReportStnParams , DA_Bv ,021 ,Bv ,021 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x33 | 1 | 1 | StationID | UINT16 |  | 355 |  |  |  | Contains the Station Number for which to start sending the station parameters. Range is 1 to 225. | 000 | Av | 355 | 0x33_StationID , DA_Av ,355 ,Av ,355 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the Station Number for which t ,
0x33 | [10 empty] | 000
0x33 | 2 | 2 | Count | Byte |  |  |  | 450 |  | Number of station paramters in this transmission. Range is 1 to 18. | 000 | Ai | 450 | 0x33_Count , DA_Ai ,450 ,Ai ,450 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Number of station paramters in this tra ,
0x33 | 3 | 3 | StationID | UINT16 |  |  |  | 451 |  | Part of Station Parameters. Contains the Station Number for the parameters being sent. Range is 1 to 225. | 000 | Ai | 451 | 0x33_StationID , DA_Ai ,451 ,Ai ,451 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x33 | 4 | 4 | PumpUsage | Byte |  |  |  | 452 |  | Part of Station Parameters. Value containing information on the pumps required to operate when the station is active. Bit 0: 1 = Pump 1 used- 0 = Pump 1 Not used. Bit 1: 1 = Pump 2 used- 0 = Pump 2 Not used. Bit 2: 1 = Pump 3 used- 0 = Pump 3 Not used. Bit 3: 1 = Pump 4 used- 0 = Pump 4 Not used. Bit 4: 1 = Pump 5 used- 0 = Pump 5 Not used. Bit 5: 1 = Pump 6 used- 0 = Pump 6 Not used. | 000 | Ai | 452 | 0x33_PumpUsage , DA_Ai ,452 ,Ai ,452 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Value conta ,
0x33 | 5 | 5 | CycleTime | UINT16 |  |  |  | 453 |  | Part of Station Parameters. Contains the maximum number of minutes to allow for a single cycle for the specified station. Rnage is 1 to 360. Not used is indicated by 0. If Cycle Rime is 0- the Soak Time will be forced to 0 regardless of value sent in command. | 000 | Ai | 453 | 0x33_CycleTime , DA_Ai ,453 ,Ai ,453 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x33 | 6 | 6 | SoakTime | UINT16 |  |  |  | 454 |  | Part of Station Parameters. Contains the minimum soak time before a subsequent cycle can begin for a station. Range is 1 to 540. Not used is indicated by 0. | 000 | Ai | 454 | 0x33_SoakTime , DA_Ai ,454 ,Ai ,454 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x33 | 7 | 7 | FlowZone | Byte |  |  |  | 455 |  | Part of Station Parameters. Contains the Flow Zone number that the station is assigned to. Range is 0 to 6. A value of 0 indicated that the station is not assigned to a Flow Zone. | 000 | Ai | 455 | 0x33_FlowZone , DA_Ai ,455 ,Ai ,455 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x33 | 8 | 8 | FlowPriority | Byte |  |  |  | 456 |  | Part of Station Parameters. Contains indication of whether or not this station is a Flow Priority. A value of 0 indicated no priority. A value of 1 indicated that it is a Flow Priority. | 000 | Ai | 456 | 0x33_FlowPriority , DA_Ai ,456 ,Ai ,456 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains in ,
0x33 | 9 | 9 | LearnedFlow | UINT16 |  |  |  | 457 |  | Part of Station Parameters. Contains the learned flow value for the station times 10. Value is in gallons and the range is 1 to 6-550.0 in steps of 0.1. A value of 0xFFEF indicates to ignore Learned Flow value for this Station. A value of 0xFFFF indicates that the station is not learned and is the default value. | 000 | Ai | 457 | 0x33_LearnedFlow , DA_Ai ,457 ,Ai ,457 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
0x33 | 10 | 10 | FlowDelay | UINT16 |  |  |  | 458 |  | Part of Station Parameters. Contains the delay tie in seconds before beginning to start flow monitoring for that station. Rance is 15 to 600. Default is 60. | 000 | Ai | 458 | 0x33_FlowDelay , DA_Ai ,458 ,Ai ,458 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of Station Parameters. Contains th ,
000
0x34 – Report Block Parameters | [10 empty] | 000 |  |  |  |  | 0x34 – Report Block Parameters
| Not Implemented | [9 empty] | 000
000
0x35 – Stop Blocks | [10 empty] | 000 |  |  |  |  | 0x35 – Stop Blocks
| Not Implemented | [9 empty] | 000
000
0x36 – REPORT PUMP/MASTER VALVE PARAMETERS (v2.11.007 and later) | [10 empty] | 000 |  |  |  |  | 0x36 – REPORT PUMP/MASTER VALVE PARAMETERS (v2.11.007 and later)
| demo=h36.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command returns all settings for each of the six Pump/Master Valve outputs in the controller and the Normally Open P/MV Exercise settings. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x36 | 0 | 1 | PmvLocation | Byte |  |  |  | 459 | P1Config | Location of the P/MV. Range is 0 to 1. 0 = P/MV Output Terminal 1 = Assigned to a Station or Decoder. | 000 | Ai | 459 | 0x36_P1ConfigPmvLocation , DA_Ai ,459 ,Ai ,459 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the P/MV. Range is 0 to 1. ,
0x36 | 1 | 2 | LocationNumber | UINT16 |  |  |  | 460 | P1Config | Assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 460 | 0x36_P1ConfigLocationNumber , DA_Ai ,460 ,Ai ,460 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Assigned location number. Range is depe ,
0x36 | 2 | 3 | PmvStyle | Byte |  |  |  | 461 | P1Config | Style of the P/MV output. | 000 | Ai | 461 | 0x36_P1ConfigPmvStyle , DA_Ai ,461 ,Ai ,461 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Style of the P/MV output. ,
0x36 | 3 | 4 | PmvOnDelay | UINT16 |  |  |  | 462 | P1Config | Seconds to delay after turning on the P/MV output before starting the station requiring the P/MV. Range is 0 to 120. | 000 | Ai | 462 | 0x36_P1ConfigPmvOnDelay , DA_Ai ,462 ,Ai ,462 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after turning on the P ,
0x36 | 4 | 5 | PmvOffDelay | UINT16 |  |  |  | 463 | P1Config | Seconds to delay after shutting off the last station requiring the P/MV before shutting off the P/MV output. Range is 3 to 60. | 000 | Ai | 463 | 0x36_P1ConfigPmvOffDelay , DA_Ai ,463 ,Ai ,463 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after shutting off the ,
0x36 | 5 | 6 | PmvExerciseEnable | Byte |  |  |  | 464 | P1Config | Enable P/MV exercising for this P/MV if style is Normally Open. Range is 0 to 1. | 000 | Ai | 464 | 0x36_P1ConfigPmvExerciseEnable , DA_Ai ,464 ,Ai ,464 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable P/MV exercising for this P/MV if ,
0x36 | 6 | 7 | PmvLocation | Byte |  |  |  | 465 | P2config | Location of the P/MV. Range is 0 to 1. 0 = P/MV Output Terminal 1 = Assigned to a Station or Decoder. | 000 | Ai | 465 | 0x36_P2configPmvLocation , DA_Ai ,465 ,Ai ,465 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the P/MV. Range is 0 to 1. ,
0x36 | 7 | 8 | LocationNumber | UINT16 |  |  |  | 466 | P2config | Assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 466 | 0x36_P2configLocationNumber , DA_Ai ,466 ,Ai ,466 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Assigned location number. Range is depe ,
0x36 | 8 | 9 | PmvStyle | Byte |  |  |  | 467 | P2config | Style of the P/MV output. | 000 | Ai | 467 | 0x36_P2configPmvStyle , DA_Ai ,467 ,Ai ,467 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Style of the P/MV output. ,
0x36 | 9 | 10 | PmvOnDelay | UINT16 |  |  |  | 468 | P2config | Seconds to delay after turning on the P/MV output before starting the station requiring the P/MV. Range is 0 to 120. | 000 | Ai | 468 | 0x36_P2configPmvOnDelay , DA_Ai ,468 ,Ai ,468 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after turning on the P ,
0x36 | 10 | 11 | PmvOffDelay | UINT16 |  |  |  | 469 | P2config | Seconds to delay after shutting off the last station requiring the P/MV before shutting off the P/MV output. Range is 3 to 60. | 000 | Ai | 469 | 0x36_P2configPmvOffDelay , DA_Ai ,469 ,Ai ,469 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after shutting off the ,
0x36 | 11 | 12 | PmvExerciseEnable | Byte |  |  |  | 470 | P2config | Enable P/MV exercising for this P/MV if style is Normally Open. Range is 0 to 1. | 000 | Ai | 470 | 0x36_P2configPmvExerciseEnable , DA_Ai ,470 ,Ai ,470 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable P/MV exercising for this P/MV if ,
0x36 | 12 | 13 | PmvLocation | Byte |  |  |  | 471 | P3config | Location of the P/MV. Range is 0 to 1. 0 = P/MV Output Terminal 1 = Assigned to a Station or Decoder. | 000 | Ai | 471 | 0x36_P3configPmvLocation , DA_Ai ,471 ,Ai ,471 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the P/MV. Range is 0 to 1. ,
0x36 | 13 | 14 | LocationNumber | UINT16 |  |  |  | 472 | P3config | Assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 472 | 0x36_P3configLocationNumber , DA_Ai ,472 ,Ai ,472 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Assigned location number. Range is depe ,
0x36 | 14 | 15 | PmvStyle | Byte |  |  |  | 473 | P3config | Style of the P/MV output. | 000 | Ai | 473 | 0x36_P3configPmvStyle , DA_Ai ,473 ,Ai ,473 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Style of the P/MV output. ,
0x36 | 15 | 16 | PmvOnDelay | UINT16 |  |  |  | 474 | P3config | Seconds to delay after turning on the P/MV output before starting the station requiring the P/MV. Range is 0 to 120. | 000 | Ai | 474 | 0x36_P3configPmvOnDelay , DA_Ai ,474 ,Ai ,474 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after turning on the P ,
0x36 | 16 | 17 | PmvOffDelay | UINT16 |  |  |  | 475 | P3config | Seconds to delay after shutting off the last station requiring the P/MV before shutting off the P/MV output. Range is 3 to 60. | 000 | Ai | 475 | 0x36_P3configPmvOffDelay , DA_Ai ,475 ,Ai ,475 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after shutting off the ,
0x36 | 17 | 18 | PmvExerciseEnable | Byte |  |  |  | 476 | P3config | Enable P/MV exercising for this P/MV if style is Normally Open. Range is 0 to 1. | 000 | Ai | 476 | 0x36_P3configPmvExerciseEnable , DA_Ai ,476 ,Ai ,476 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable P/MV exercising for this P/MV if ,
0x36 | 18 | 19 | PmvLocation | Byte |  |  |  | 477 | P4config | Location of the P/MV. Range is 0 to 1. 0 = P/MV Output Terminal 1 = Assigned to a Station or Decoder. | 000 | Ai | 477 | 0x36_P4configPmvLocation , DA_Ai ,477 ,Ai ,477 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the P/MV. Range is 0 to 1. ,
0x36 | 19 | 20 | LocationNumber | UINT16 |  |  |  | 478 | P4config | Assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 478 | 0x36_P4configLocationNumber , DA_Ai ,478 ,Ai ,478 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Assigned location number. Range is depe ,
0x36 | 20 | 21 | PmvStyle | Byte |  |  |  | 479 | P4config | Style of the P/MV output. | 000 | Ai | 479 | 0x36_P4configPmvStyle , DA_Ai ,479 ,Ai ,479 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Style of the P/MV output. ,
0x36 | 21 | 22 | PmvOnDelay | UINT16 |  |  |  | 480 | P4config | Seconds to delay after turning on the P/MV output before starting the station requiring the P/MV. Range is 0 to 120. | 000 | Ai | 480 | 0x36_P4configPmvOnDelay , DA_Ai ,480 ,Ai ,480 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after turning on the P ,
0x36 | 22 | 23 | PmvOffDelay | UINT16 |  |  |  | 481 | P4config | Seconds to delay after shutting off the last station requiring the P/MV before shutting off the P/MV output. Range is 3 to 60. | 000 | Ai | 481 | 0x36_P4configPmvOffDelay , DA_Ai ,481 ,Ai ,481 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after shutting off the ,
0x36 | 23 | 24 | PmvExerciseEnable | Byte |  |  |  | 482 | P4config | Enable P/MV exercising for this P/MV if style is Normally Open. Range is 0 to 1. | 000 | Ai | 482 | 0x36_P4configPmvExerciseEnable , DA_Ai ,482 ,Ai ,482 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable P/MV exercising for this P/MV if ,
0x36 | 24 | 25 | PmvLocation | Byte |  |  |  | 483 | P5config | Location of the P/MV. Range is 0 to 1. 0 = P/MV Output Terminal 1 = Assigned to a Station or Decoder. | 000 | Ai | 483 | 0x36_P5configPmvLocation , DA_Ai ,483 ,Ai ,483 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the P/MV. Range is 0 to 1. ,
0x36 | 25 | 26 | LocationNumber | UINT16 |  |  |  | 484 | P5config | Assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 484 | 0x36_P5configLocationNumber , DA_Ai ,484 ,Ai ,484 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Assigned location number. Range is depe ,
0x36 | 26 | 27 | PmvStyle | Byte |  |  |  | 485 | P5config | Style of the P/MV output. | 000 | Ai | 485 | 0x36_P5configPmvStyle , DA_Ai ,485 ,Ai ,485 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Style of the P/MV output. ,
0x36 | 27 | 28 | PmvOnDelay | UINT16 |  |  |  | 486 | P5config | Seconds to delay after turning on the P/MV output before starting the station requiring the P/MV. Range is 0 to 120. | 000 | Ai | 486 | 0x36_P5configPmvOnDelay , DA_Ai ,486 ,Ai ,486 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after turning on the P ,
0x36 | 28 | 29 | PmvOffDelay | UINT16 |  |  |  | 487 | P5config | Seconds to delay after shutting off the last station requiring the P/MV before shutting off the P/MV output. Range is 3 to 60. | 000 | Ai | 487 | 0x36_P5configPmvOffDelay , DA_Ai ,487 ,Ai ,487 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after shutting off the ,
0x36 | 29 | 30 | PmvExerciseEnable | Byte |  |  |  | 488 | P5config | Enable P/MV exercising for this P/MV if style is Normally Open. Range is 0 to 1. | 000 | Ai | 488 | 0x36_P5configPmvExerciseEnable , DA_Ai ,488 ,Ai ,488 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable P/MV exercising for this P/MV if ,
0x36 | 30 | 31 | PmvLocation | Byte |  |  |  | 489 | P6config | Location of the P/MV. Range is 0 to 1. 0 = P/MV Output Terminal 1 = Assigned to a Station or Decoder. | 000 | Ai | 489 | 0x36_P6configPmvLocation , DA_Ai ,489 ,Ai ,489 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the P/MV. Range is 0 to 1. ,
0x36 | 31 | 32 | LocationNumber | UINT16 |  |  |  | 490 | P6config | Assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 490 | 0x36_P6configLocationNumber , DA_Ai ,490 ,Ai ,490 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Assigned location number. Range is depe ,
0x36 | 32 | 33 | PmvStyle | Byte |  |  |  | 491 | P6config | Style of the P/MV output. | 000 | Ai | 491 | 0x36_P6configPmvStyle , DA_Ai ,491 ,Ai ,491 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Style of the P/MV output. ,
0x36 | 33 | 34 | PmvOnDelay | UINT16 |  |  |  | 492 | P6config | Seconds to delay after turning on the P/MV output before starting the station requiring the P/MV. Range is 0 to 120. | 000 | Ai | 492 | 0x36_P6configPmvOnDelay , DA_Ai ,492 ,Ai ,492 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after turning on the P ,
0x36 | 34 | 35 | PmvOffDelay | UINT16 |  |  |  | 493 | P6config | Seconds to delay after shutting off the last station requiring the P/MV before shutting off the P/MV output. Range is 3 to 60. | 000 | Ai | 493 | 0x36_P6configPmvOffDelay , DA_Ai ,493 ,Ai ,493 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds to delay after shutting off the ,
0x36 | 35 | 36 | PmvExerciseEnable | Byte |  |  |  | 494 | P6config | Enable P/MV exercising for this P/MV if style is Normally Open. Range is 0 to 1. | 000 | Ai | 494 | 0x36_P6configPmvExerciseEnable , DA_Ai ,494 ,Ai ,494 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Enable P/MV exercising for this P/MV if ,
0x36 | 36 | 37 | PmvExerciseInterval | UINT16 |  |  |  | 495 |  | Interval in days that all Normally Open P/MVs should be exercised. Range is 1 to 31. Default is 31. | 000 | Ai | 495 | 0x36_PmvExerciseInterval , DA_Ai ,495 ,Ai ,495 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Interval in days that all Normally Open ,
0x36 | 37 | 38 | PmvExerciseNext | UINT16 |  |  |  | 496 |  | Days before next Normally Open P/MV Exercise. Range is 0 to 30. Must be at least one less than exercise interval length. A value of 0xFF will be returned if exercise schedule has not yet been established. | 000 | Ai | 496 | 0x36_PmvExerciseNext , DA_Ai ,496 ,Ai ,496 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Days before next Normally Open P/MV Exe ,
0x36 | 38 | 39 | PmvExerciseStartTime | Byte |  |  |  | 497 |  | Time in MAM that all Normally Open P/MVs should be exercised. Range is 0 – 1439. OFF is indicated by FFFFH. Default is 720 (12pm). | 000 | Ai | 497 | 0x36_PmvExerciseStartTime , DA_Ai ,497 ,Ai ,497 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Time in MAM that all Normally Open P/MV ,
000
0x37 – Reserved for Future | [10 empty] | 000 |  |  |  |  | 0x37 – Reserved for Future
000
000
0x38 – SET LEARN FLOW START/STOP TIME | [10 empty] | 000 |  |  |  |  | 0x38 – SET LEARN FLOW START/STOP TIME
| demo=h38.html | [9 empty] | 000
| template=Type3 | [9 empty] | 000
| This command sends a date/time for the controller to automatically perform a flow learning process. | [9 empty] | 000
| Errnum=6 | [9 empty] | 000
| Data Array | Payload | [8 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x38 | 0 |  | Trigger_SetLearnFlowStart |  | 22 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 22 | 0x38_Trigger_SetLearnFlowStart , DA_Bv ,022 ,Bv ,022 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x38 | 1 | 1 | StartTime | UINT32 |  | 356 |  |  |  | Unsigned value representing the date/time to start the flow learning process. Value sent should be to nearest minute- but is not a requirement. Controller will only test to minute level when determining if it is time to start the learn process automatically. A value of 0 indicates to start immediately. A value of 0xFFFFFFFF indicates start time is OFF. Valid range for actual time value sent is from the current UnixTime through up to 365 days of seconds in the future | 000 | Av | 356 | 0x38_StartTime , DA_Av ,356 ,Av ,356 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the date/ti ,
000
000
000
0x39 – GET LEARN FLOW STATUS INFO | [10 empty] | 000 |  |  |  |  | 0x39 – GET LEARN FLOW STATUS INFO
| demo=h39.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command reports the status of the flow learning process. If flow learning is active, will have the latest status data from the current process. If flow learning is not active, will have the results from the last flow learn process performed. | [9 empty] | 000
| Errnum=6 | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x39 | 1 | 1 | StartTime | UINT32 |  |  |  | 498 |  | Unsigned value representing the date/time to start the flow learning process. Value sent should be to nearest minute- but is not a requirement. Controller will only test to minute level when determining if it is time to start the learn process automatically. A value of 0 indicates to start immediately. A value of 0xFFFFFFFF indicates start time is OFF. Valid range for actual time value sent is from the current UnixTime through up to 365 days of seconds in the future | 000 | Ai | 498 | 0x39_StartTime , DA_Ai ,498 ,Ai ,498 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the date/ti ,
0x39 | 2 | 2 | Active | Byte |  |  |  | 499 |  | Part of P1Config. Value indicating the assigned location number. Range is dependent upon the PmvLocation value. | 000 | Ai | 499 | 0x39_Active , DA_Ai ,499 ,Ai ,499 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Part of P1Config. Value indicating the ,
0x39 | 3 | 3 | LastRun | UINT32 |  |  |  | 500 |  | Unsigned value representing the Unix date/time the last time flow learning was run. A value of 0 indicates that the flow learn process has never been run and all remaining bytes should be ignored. | 000 | Ai | 500 | 0x39_LastRun , DA_Ai ,500 ,Ai ,500 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unix da ,
0x39 | 4 | 4 | CurrentStation | UINT16 |  |  |  | 501 |  | Value indicating the current station number running as part of the flow learn process. Range is 0 to 225. A value of 0 will be returned if the flow learn process is not active | 000 | Ai | 501 | 0x39_CurrentStation , DA_Ai ,501 ,Ai ,501 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current station nu ,
0x39 | 5 | 5 | LastFlowRead | UINT16 |  |  |  | 502 |  | Value indicating the last flow reading taken for the current station during the flow learn process. Value is GPM x 10. Range is 0 to 65500 | 000 | Ai | 502 | 0x39_LastFlowRead , DA_Ai ,502 ,Ai ,502 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the last flow reading ,
0x39 | 6 | 6 | StasProcessed | UINT16 |  |  |  | 503 |  | Value indicating the number of stations that have been processed during the flow learn process. Range is 0 to 225. | 000 | Ai | 503 | 0x39_StasProcessed , DA_Ai ,503 ,Ai ,503 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x39 | 7 | 7 | StasToLearn | UINT16 |  |  |  | 504 |  | Value indicating the number of stations to be learned. Range is 0 to 225. | 000 | Ai | 504 | 0x39_StasToLearn , DA_Ai ,504 ,Ai ,504 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x39 | 8 | 8 | StasLearned | UINT16 |  |  |  | 505 |  | Value indicating the number of stations that were successfully learned. Range is 0 to 225 | 000 | Ai | 505 | 0x39_StasLearned , DA_Ai ,505 ,Ai ,505 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x39 | 9 | 9 | StasFailed | UINT16 |  |  |  | 506 |  | Value indicating the number of stations that failed to have their flow learned. Range is 0 to 225. | 000 | Ai | 506 | 0x39_StasFailed , DA_Ai ,506 ,Ai ,506 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
000
000
0x3A – Get Learn Flow Report Info | [10 empty] | 000 |  |  |  |  | 0x3A – Get Learn Flow Report Info
| demo=h3a.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| This command returns the last learn flow report data to the central. Data is only available if the flow learn process is not active. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x3A | 1 | 1 | Active | Byte |  |  |  | 507 |  | Indicates whether or not flow learning is currently active. 0 – Indicates that flow learning is not active. 1 – Indicates that flow learning is active- and all remaining bytes should be ignored. | 000 | Ai | 507 | 0x3A_Active , DA_Ai ,507 ,Ai ,507 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Indicates whether or not flow learning ,
0x3A | 2 | 2 | StasWithRunTime | UINT16 |  |  |  | 508 |  | Value indicating the number of stations that had a run time assigned in one or more programs at the time of the learn process. Range is 0 to 225. | 000 | Ai | 508 | 0x3A_StasWithRunTime , DA_Ai ,508 ,Ai ,508 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x3A | 3 | 3 | StasMonitored | UINT16 |  |  |  | 509 |  | Value indicating the number of stations that were assigned to a flow monitored Flow Zone at the time of the learn process. Range is 0 to 22 | 000 | Ai | 509 | 0x3A_StasMonitored , DA_Ai ,509 ,Ai ,509 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x3A | 4 | 4 | StasWithFlowRate | UINT16 |  |  |  | 510 |  | Value indicating the number of stations that already had a flow rate stored at the time of the learn process. Range is 0 to 225. | 000 | Ai | 510 | 0x3A_StasWithFlowRate , DA_Ai ,510 ,Ai ,510 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x3A | 5 | 5 | StasToLearn | UINT16 |  |  |  | 511 |  | Value indicating the number of stations to be learned. Range is 0 to 225 | 000 | Ai | 511 | 0x3A_StasToLearn , DA_Ai ,511 ,Ai ,511 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x3A | 6 | 6 | StasLearned | UINT16 |  |  |  | 512 |  | Value indicating the number of stations that were successfully learned. Range is 0 to 225 | 000 | Ai | 512 | 0x3A_StasLearned , DA_Ai ,512 ,Ai ,512 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x3A | 7 | 7 | StasFailed | UINT16 |  |  |  | 513 |  | Value indicating the number of stations that failed to have their flow learned. Range is 0 to 225. | 000 | Ai | 513 | 0x3A_StasFailed , DA_Ai ,513 ,Ai ,513 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of stations ,
0x3A | 8 | 8 | FlowSenCfg | Byte |  |  |  | 514 |  | Value indicating the number of Flow Sensors configured at the time of the learn process. Range is 1 to 6. | 000 | Ai | 514 | 0x3A_FlowSenCfg , DA_Ai ,514 ,Ai ,514 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of Flow Sen ,
0x3A | 9 | 9 | StaStatus #1 | Byte |  |  |  | 515 |  | Value indicating the final status of each station after the learn process completed. Range is 0 to 7. 0 = Unknown (Most likely a station above controller size) 1 = Station did not have a run time in any program 2 = Station was not assigned to a flow monitored Flow Zone 3 = Station does not have a flow rate (not learned) 4 = Station already had a flow rate 5 = Station flow rate was successfully learned 6 = Station failed to learn during a previous learn process 7 = Station failed to learn during the last learn process | 000 | Ai | 515 | 0x3A_StaStatus #1 , DA_Ai ,515 ,Ai ,515 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the final status of ea ,
0x3A | 10 | 10 | StaStatus #2 | Byte |  |  |  | 516 |  | Ditto | 000 | Ai | 516 | 0x3A_StaStatus #2 , DA_Ai ,516 ,Ai ,516 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 11 | 11 | StaStatus #3 | Byte |  |  |  | 517 |  | Ditto | 000 | Ai | 517 | 0x3A_StaStatus #3 , DA_Ai ,517 ,Ai ,517 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 12 | 12 | StaStatus #4 | Byte |  |  |  | 518 |  | Ditto | 000 | Ai | 518 | 0x3A_StaStatus #4 , DA_Ai ,518 ,Ai ,518 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 13 | 13 | StaStatus #5 | Byte |  |  |  | 519 |  | Ditto | 000 | Ai | 519 | 0x3A_StaStatus #5 , DA_Ai ,519 ,Ai ,519 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 14 | 14 | StaStatus #6 | Byte |  |  |  | 520 |  | Ditto | 000 | Ai | 520 | 0x3A_StaStatus #6 , DA_Ai ,520 ,Ai ,520 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 15 | 15 | StaStatus #7 | Byte |  |  |  | 521 |  | Ditto | 000 | Ai | 521 | 0x3A_StaStatus #7 , DA_Ai ,521 ,Ai ,521 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 16 | 16 | StaStatus #8 | Byte |  |  |  | 522 |  | Ditto | 000 | Ai | 522 | 0x3A_StaStatus #8 , DA_Ai ,522 ,Ai ,522 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 17 | 17 | StaStatus #9 | Byte |  |  |  | 523 |  | Ditto | 000 | Ai | 523 | 0x3A_StaStatus #9 , DA_Ai ,523 ,Ai ,523 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 18 | 18 | StaStatus #10 | Byte |  |  |  | 524 |  | Ditto | 000 | Ai | 524 | 0x3A_StaStatus #10 , DA_Ai ,524 ,Ai ,524 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 19 | 19 | StaStatus #11 | Byte |  |  |  | 525 |  | Ditto | 000 | Ai | 525 | 0x3A_StaStatus #11 , DA_Ai ,525 ,Ai ,525 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 20 | 20 | StaStatus #12 | Byte |  |  |  | 526 |  | Ditto | 000 | Ai | 526 | 0x3A_StaStatus #12 , DA_Ai ,526 ,Ai ,526 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 21 | 21 | StaStatus #13 | Byte |  |  |  | 527 |  | Ditto | 000 | Ai | 527 | 0x3A_StaStatus #13 , DA_Ai ,527 ,Ai ,527 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 22 | 22 | StaStatus #14 | Byte |  |  |  | 528 |  | Ditto | 000 | Ai | 528 | 0x3A_StaStatus #14 , DA_Ai ,528 ,Ai ,528 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 23 | 23 | StaStatus #15 | Byte |  |  |  | 529 |  | Ditto | 000 | Ai | 529 | 0x3A_StaStatus #15 , DA_Ai ,529 ,Ai ,529 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 24 | 24 | StaStatus #16 | Byte |  |  |  | 530 |  | Ditto | 000 | Ai | 530 | 0x3A_StaStatus #16 , DA_Ai ,530 ,Ai ,530 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 25 | 25 | StaStatus #17 | Byte |  |  |  | 531 |  | Ditto | 000 | Ai | 531 | 0x3A_StaStatus #17 , DA_Ai ,531 ,Ai ,531 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 26 | 26 | StaStatus #18 | Byte |  |  |  | 532 |  | Ditto | 000 | Ai | 532 | 0x3A_StaStatus #18 , DA_Ai ,532 ,Ai ,532 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 27 | 27 | StaStatus #19 | Byte |  |  |  | 533 |  | Ditto | 000 | Ai | 533 | 0x3A_StaStatus #19 , DA_Ai ,533 ,Ai ,533 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 28 | 28 | StaStatus #20 | Byte |  |  |  | 534 |  | Ditto | 000 | Ai | 534 | 0x3A_StaStatus #20 , DA_Ai ,534 ,Ai ,534 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 29 | 29 | StaStatus #21 | Byte |  |  |  | 535 |  | Ditto | 000 | Ai | 535 | 0x3A_StaStatus #21 , DA_Ai ,535 ,Ai ,535 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 30 | 30 | StaStatus #22 | Byte |  |  |  | 536 |  | Ditto | 000 | Ai | 536 | 0x3A_StaStatus #22 , DA_Ai ,536 ,Ai ,536 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 31 | 31 | StaStatus #23 | Byte |  |  |  | 537 |  | Ditto | 000 | Ai | 537 | 0x3A_StaStatus #23 , DA_Ai ,537 ,Ai ,537 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 32 | 32 | StaStatus #24 | Byte |  |  |  | 538 |  | Ditto | 000 | Ai | 538 | 0x3A_StaStatus #24 , DA_Ai ,538 ,Ai ,538 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 33 | 33 | StaStatus #25 | Byte |  |  |  | 539 |  | Ditto | 000 | Ai | 539 | 0x3A_StaStatus #25 , DA_Ai ,539 ,Ai ,539 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 34 | 34 | StaStatus #26 | Byte |  |  |  | 540 |  | Ditto | 000 | Ai | 540 | 0x3A_StaStatus #26 , DA_Ai ,540 ,Ai ,540 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 35 | 35 | StaStatus #27 | Byte |  |  |  | 541 |  | Ditto | 000 | Ai | 541 | 0x3A_StaStatus #27 , DA_Ai ,541 ,Ai ,541 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 36 | 36 | StaStatus #28 | Byte |  |  |  | 542 |  | Ditto | 000 | Ai | 542 | 0x3A_StaStatus #28 , DA_Ai ,542 ,Ai ,542 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 37 | 37 | StaStatus #29 | Byte |  |  |  | 543 |  | Ditto | 000 | Ai | 543 | 0x3A_StaStatus #29 , DA_Ai ,543 ,Ai ,543 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 38 | 38 | StaStatus #30 | Byte |  |  |  | 544 |  | Ditto | 000 | Ai | 544 | 0x3A_StaStatus #30 , DA_Ai ,544 ,Ai ,544 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 39 | 39 | StaStatus #31 | Byte |  |  |  | 545 |  | Ditto | 000 | Ai | 545 | 0x3A_StaStatus #31 , DA_Ai ,545 ,Ai ,545 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 40 | 40 | StaStatus #32 | Byte |  |  |  | 546 |  | Ditto | 000 | Ai | 546 | 0x3A_StaStatus #32 , DA_Ai ,546 ,Ai ,546 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 41 | 41 | StaStatus #33 | Byte |  |  |  | 547 |  | Ditto | 000 | Ai | 547 | 0x3A_StaStatus #33 , DA_Ai ,547 ,Ai ,547 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 42 | 42 | StaStatus #34 | Byte |  |  |  | 548 |  | Ditto | 000 | Ai | 548 | 0x3A_StaStatus #34 , DA_Ai ,548 ,Ai ,548 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 43 | 43 | StaStatus #35 | Byte |  |  |  | 549 |  | Ditto | 000 | Ai | 549 | 0x3A_StaStatus #35 , DA_Ai ,549 ,Ai ,549 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 44 | 44 | StaStatus #36 | Byte |  |  |  | 550 |  | Ditto | 000 | Ai | 550 | 0x3A_StaStatus #36 , DA_Ai ,550 ,Ai ,550 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 45 | 45 | StaStatus #37 | Byte |  |  |  | 551 |  | Ditto | 000 | Ai | 551 | 0x3A_StaStatus #37 , DA_Ai ,551 ,Ai ,551 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 46 | 46 | StaStatus #38 | Byte |  |  |  | 552 |  | Ditto | 000 | Ai | 552 | 0x3A_StaStatus #38 , DA_Ai ,552 ,Ai ,552 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 47 | 47 | StaStatus #39 | Byte |  |  |  | 553 |  | Ditto | 000 | Ai | 553 | 0x3A_StaStatus #39 , DA_Ai ,553 ,Ai ,553 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 48 | 48 | StaStatus #40 | Byte |  |  |  | 554 |  | Ditto | 000 | Ai | 554 | 0x3A_StaStatus #40 , DA_Ai ,554 ,Ai ,554 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 49 | 49 | StaStatus #41 | Byte |  |  |  | 555 |  | Ditto | 000 | Ai | 555 | 0x3A_StaStatus #41 , DA_Ai ,555 ,Ai ,555 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 50 | 50 | StaStatus #42 | Byte |  |  |  | 556 |  | Ditto | 000 | Ai | 556 | 0x3A_StaStatus #42 , DA_Ai ,556 ,Ai ,556 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 51 | 51 | StaStatus #43 | Byte |  |  |  | 557 |  | Ditto | 000 | Ai | 557 | 0x3A_StaStatus #43 , DA_Ai ,557 ,Ai ,557 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 52 | 52 | StaStatus #44 | Byte |  |  |  | 558 |  | Ditto | 000 | Ai | 558 | 0x3A_StaStatus #44 , DA_Ai ,558 ,Ai ,558 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 53 | 53 | StaStatus #45 | Byte |  |  |  | 559 |  | Ditto | 000 | Ai | 559 | 0x3A_StaStatus #45 , DA_Ai ,559 ,Ai ,559 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 54 | 54 | StaStatus #46 | Byte |  |  |  | 560 |  | Ditto | 000 | Ai | 560 | 0x3A_StaStatus #46 , DA_Ai ,560 ,Ai ,560 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 55 | 55 | StaStatus #47 | Byte |  |  |  | 561 |  | Ditto | 000 | Ai | 561 | 0x3A_StaStatus #47 , DA_Ai ,561 ,Ai ,561 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 56 | 56 | StaStatus #48 | Byte |  |  |  | 562 |  | Ditto | 000 | Ai | 562 | 0x3A_StaStatus #48 , DA_Ai ,562 ,Ai ,562 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 57 | 57 | StaStatus #49 | Byte |  |  |  | 563 |  | Ditto | 000 | Ai | 563 | 0x3A_StaStatus #49 , DA_Ai ,563 ,Ai ,563 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 58 | 58 | StaStatus #50 | Byte |  |  |  | 564 |  | Ditto | 000 | Ai | 564 | 0x3A_StaStatus #50 , DA_Ai ,564 ,Ai ,564 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 59 | 59 | StaStatus #51 | Byte |  |  |  | 565 |  | Ditto | 000 | Ai | 565 | 0x3A_StaStatus #51 , DA_Ai ,565 ,Ai ,565 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 60 | 60 | StaStatus #52 | Byte |  |  |  | 566 |  | Ditto | 000 | Ai | 566 | 0x3A_StaStatus #52 , DA_Ai ,566 ,Ai ,566 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 61 | 61 | StaStatus #53 | Byte |  |  |  | 567 |  | Ditto | 000 | Ai | 567 | 0x3A_StaStatus #53 , DA_Ai ,567 ,Ai ,567 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 62 | 62 | StaStatus #54 | Byte |  |  |  | 568 |  | Ditto | 000 | Ai | 568 | 0x3A_StaStatus #54 , DA_Ai ,568 ,Ai ,568 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 63 | 63 | StaStatus #55 | Byte |  |  |  | 569 |  | Ditto | 000 | Ai | 569 | 0x3A_StaStatus #55 , DA_Ai ,569 ,Ai ,569 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 64 | 64 | StaStatus #56 | Byte |  |  |  | 570 |  | Ditto | 000 | Ai | 570 | 0x3A_StaStatus #56 , DA_Ai ,570 ,Ai ,570 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 65 | 65 | StaStatus #57 | Byte |  |  |  | 571 |  | Ditto | 000 | Ai | 571 | 0x3A_StaStatus #57 , DA_Ai ,571 ,Ai ,571 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 66 | 66 | StaStatus #58 | Byte |  |  |  | 572 |  | Ditto | 000 | Ai | 572 | 0x3A_StaStatus #58 , DA_Ai ,572 ,Ai ,572 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 67 | 67 | StaStatus #59 | Byte |  |  |  | 573 |  | Ditto | 000 | Ai | 573 | 0x3A_StaStatus #59 , DA_Ai ,573 ,Ai ,573 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 68 | 68 | StaStatus #60 | Byte |  |  |  | 574 |  | Ditto | 000 | Ai | 574 | 0x3A_StaStatus #60 , DA_Ai ,574 ,Ai ,574 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 69 | 69 | StaStatus #61 | Byte |  |  |  | 575 |  | Ditto | 000 | Ai | 575 | 0x3A_StaStatus #61 , DA_Ai ,575 ,Ai ,575 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 70 | 70 | StaStatus #62 | Byte |  |  |  | 576 |  | Ditto | 000 | Ai | 576 | 0x3A_StaStatus #62 , DA_Ai ,576 ,Ai ,576 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 71 | 71 | StaStatus #63 | Byte |  |  |  | 577 |  | Ditto | 000 | Ai | 577 | 0x3A_StaStatus #63 , DA_Ai ,577 ,Ai ,577 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 72 | 72 | StaStatus #64 | Byte |  |  |  | 578 |  | Ditto | 000 | Ai | 578 | 0x3A_StaStatus #64 , DA_Ai ,578 ,Ai ,578 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 73 | 73 | StaStatus #65 | Byte |  |  |  | 579 |  | Ditto | 000 | Ai | 579 | 0x3A_StaStatus #65 , DA_Ai ,579 ,Ai ,579 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 74 | 74 | StaStatus #66 | Byte |  |  |  | 580 |  | Ditto | 000 | Ai | 580 | 0x3A_StaStatus #66 , DA_Ai ,580 ,Ai ,580 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 75 | 75 | StaStatus #67 | Byte |  |  |  | 581 |  | Ditto | 000 | Ai | 581 | 0x3A_StaStatus #67 , DA_Ai ,581 ,Ai ,581 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 76 | 76 | StaStatus #68 | Byte |  |  |  | 582 |  | Ditto | 000 | Ai | 582 | 0x3A_StaStatus #68 , DA_Ai ,582 ,Ai ,582 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 77 | 77 | StaStatus #69 | Byte |  |  |  | 583 |  | Ditto | 000 | Ai | 583 | 0x3A_StaStatus #69 , DA_Ai ,583 ,Ai ,583 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 78 | 78 | StaStatus #70 | Byte |  |  |  | 584 |  | Ditto | 000 | Ai | 584 | 0x3A_StaStatus #70 , DA_Ai ,584 ,Ai ,584 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 79 | 79 | StaStatus #71 | Byte |  |  |  | 585 |  | Ditto | 000 | Ai | 585 | 0x3A_StaStatus #71 , DA_Ai ,585 ,Ai ,585 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 80 | 80 | StaStatus #72 | Byte |  |  |  | 586 |  | Ditto | 000 | Ai | 586 | 0x3A_StaStatus #72 , DA_Ai ,586 ,Ai ,586 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 81 | 81 | StaStatus #73 | Byte |  |  |  | 587 |  | Ditto | 000 | Ai | 587 | 0x3A_StaStatus #73 , DA_Ai ,587 ,Ai ,587 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 82 | 82 | StaStatus #74 | Byte |  |  |  | 588 |  | Ditto | 000 | Ai | 588 | 0x3A_StaStatus #74 , DA_Ai ,588 ,Ai ,588 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 83 | 83 | StaStatus #75 | Byte |  |  |  | 589 |  | Ditto | 000 | Ai | 589 | 0x3A_StaStatus #75 , DA_Ai ,589 ,Ai ,589 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 84 | 84 | StaStatus #76 | Byte |  |  |  | 590 |  | Ditto | 000 | Ai | 590 | 0x3A_StaStatus #76 , DA_Ai ,590 ,Ai ,590 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 85 | 85 | StaStatus #77 | Byte |  |  |  | 591 |  | Ditto | 000 | Ai | 591 | 0x3A_StaStatus #77 , DA_Ai ,591 ,Ai ,591 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 86 | 86 | StaStatus #78 | Byte |  |  |  | 592 |  | Ditto | 000 | Ai | 592 | 0x3A_StaStatus #78 , DA_Ai ,592 ,Ai ,592 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 87 | 87 | StaStatus #79 | Byte |  |  |  | 593 |  | Ditto | 000 | Ai | 593 | 0x3A_StaStatus #79 , DA_Ai ,593 ,Ai ,593 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 88 | 88 | StaStatus #80 | Byte |  |  |  | 594 |  | Ditto | 000 | Ai | 594 | 0x3A_StaStatus #80 , DA_Ai ,594 ,Ai ,594 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 89 | 89 | StaStatus #81 | Byte |  |  |  | 595 |  | Ditto | 000 | Ai | 595 | 0x3A_StaStatus #81 , DA_Ai ,595 ,Ai ,595 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 90 | 90 | StaStatus #82 | Byte |  |  |  | 596 |  | Ditto | 000 | Ai | 596 | 0x3A_StaStatus #82 , DA_Ai ,596 ,Ai ,596 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 91 | 91 | StaStatus #83 | Byte |  |  |  | 597 |  | Ditto | 000 | Ai | 597 | 0x3A_StaStatus #83 , DA_Ai ,597 ,Ai ,597 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 92 | 92 | StaStatus #84 | Byte |  |  |  | 598 |  | Ditto | 000 | Ai | 598 | 0x3A_StaStatus #84 , DA_Ai ,598 ,Ai ,598 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 93 | 93 | StaStatus #85 | Byte |  |  |  | 599 |  | Ditto | 000 | Ai | 599 | 0x3A_StaStatus #85 , DA_Ai ,599 ,Ai ,599 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 94 | 94 | StaStatus #86 | Byte |  |  |  | 600 |  | Ditto | 000 | Ai | 600 | 0x3A_StaStatus #86 , DA_Ai ,600 ,Ai ,600 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 95 | 95 | StaStatus #87 | Byte |  |  |  | 601 |  | Ditto | 000 | Ai | 601 | 0x3A_StaStatus #87 , DA_Ai ,601 ,Ai ,601 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 96 | 96 | StaStatus #88 | Byte |  |  |  | 602 |  | Ditto | 000 | Ai | 602 | 0x3A_StaStatus #88 , DA_Ai ,602 ,Ai ,602 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 97 | 97 | StaStatus #89 | Byte |  |  |  | 603 |  | Ditto | 000 | Ai | 603 | 0x3A_StaStatus #89 , DA_Ai ,603 ,Ai ,603 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 98 | 98 | StaStatus #90 | Byte |  |  |  | 604 |  | Ditto | 000 | Ai | 604 | 0x3A_StaStatus #90 , DA_Ai ,604 ,Ai ,604 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 99 | 99 | StaStatus #91 | Byte |  |  |  | 605 |  | Ditto | 000 | Ai | 605 | 0x3A_StaStatus #91 , DA_Ai ,605 ,Ai ,605 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 100 | 100 | StaStatus #92 | Byte |  |  |  | 606 |  | Ditto | 000 | Ai | 606 | 0x3A_StaStatus #92 , DA_Ai ,606 ,Ai ,606 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 101 | 101 | StaStatus #93 | Byte |  |  |  | 607 |  | Ditto | 000 | Ai | 607 | 0x3A_StaStatus #93 , DA_Ai ,607 ,Ai ,607 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 102 | 102 | StaStatus #94 | Byte |  |  |  | 608 |  | Ditto | 000 | Ai | 608 | 0x3A_StaStatus #94 , DA_Ai ,608 ,Ai ,608 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 103 | 103 | StaStatus #95 | Byte |  |  |  | 609 |  | Ditto | 000 | Ai | 609 | 0x3A_StaStatus #95 , DA_Ai ,609 ,Ai ,609 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 104 | 104 | StaStatus #96 | Byte |  |  |  | 610 |  | Ditto | 000 | Ai | 610 | 0x3A_StaStatus #96 , DA_Ai ,610 ,Ai ,610 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 105 | 105 | StaStatus #97 | Byte |  |  |  | 611 |  | Ditto | 000 | Ai | 611 | 0x3A_StaStatus #97 , DA_Ai ,611 ,Ai ,611 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 106 | 106 | StaStatus #98 | Byte |  |  |  | 612 |  | Ditto | 000 | Ai | 612 | 0x3A_StaStatus #98 , DA_Ai ,612 ,Ai ,612 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 107 | 107 | StaStatus #99 | Byte |  |  |  | 613 |  | Ditto | 000 | Ai | 613 | 0x3A_StaStatus #99 , DA_Ai ,613 ,Ai ,613 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 108 | 108 | StaStatus #100 | Byte |  |  |  | 614 |  | Ditto | 000 | Ai | 614 | 0x3A_StaStatus #100 , DA_Ai ,614 ,Ai ,614 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 109 | 109 | StaStatus #101 | Byte |  |  |  | 615 |  | Ditto | 000 | Ai | 615 | 0x3A_StaStatus #101 , DA_Ai ,615 ,Ai ,615 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 110 | 110 | StaStatus #102 | Byte |  |  |  | 616 |  | Ditto | 000 | Ai | 616 | 0x3A_StaStatus #102 , DA_Ai ,616 ,Ai ,616 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 111 | 111 | StaStatus #103 | Byte |  |  |  | 617 |  | Ditto | 000 | Ai | 617 | 0x3A_StaStatus #103 , DA_Ai ,617 ,Ai ,617 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 112 | 112 | StaStatus #104 | Byte |  |  |  | 618 |  | Ditto | 000 | Ai | 618 | 0x3A_StaStatus #104 , DA_Ai ,618 ,Ai ,618 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 113 | 113 | StaStatus #105 | Byte |  |  |  | 619 |  | Ditto | 000 | Ai | 619 | 0x3A_StaStatus #105 , DA_Ai ,619 ,Ai ,619 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 114 | 114 | StaStatus #106 | Byte |  |  |  | 620 |  | Ditto | 000 | Ai | 620 | 0x3A_StaStatus #106 , DA_Ai ,620 ,Ai ,620 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 115 | 115 | StaStatus #107 | Byte |  |  |  | 621 |  | Ditto | 000 | Ai | 621 | 0x3A_StaStatus #107 , DA_Ai ,621 ,Ai ,621 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 116 | 116 | StaStatus #108 | Byte |  |  |  | 622 |  | Ditto | 000 | Ai | 622 | 0x3A_StaStatus #108 , DA_Ai ,622 ,Ai ,622 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 117 | 117 | StaStatus #109 | Byte |  |  |  | 623 |  | Ditto | 000 | Ai | 623 | 0x3A_StaStatus #109 , DA_Ai ,623 ,Ai ,623 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 118 | 118 | StaStatus #110 | Byte |  |  |  | 624 |  | Ditto | 000 | Ai | 624 | 0x3A_StaStatus #110 , DA_Ai ,624 ,Ai ,624 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 119 | 119 | StaStatus #111 | Byte |  |  |  | 625 |  | Ditto | 000 | Ai | 625 | 0x3A_StaStatus #111 , DA_Ai ,625 ,Ai ,625 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 120 | 120 | StaStatus #112 | Byte |  |  |  | 626 |  | Ditto | 000 | Ai | 626 | 0x3A_StaStatus #112 , DA_Ai ,626 ,Ai ,626 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 121 | 121 | StaStatus #113 | Byte |  |  |  | 627 |  | Ditto | 000 | Ai | 627 | 0x3A_StaStatus #113 , DA_Ai ,627 ,Ai ,627 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 122 | 122 | StaStatus #114 | Byte |  |  |  | 628 |  | Ditto | 000 | Ai | 628 | 0x3A_StaStatus #114 , DA_Ai ,628 ,Ai ,628 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 123 | 123 | StaStatus #115 | Byte |  |  |  | 629 |  | Ditto | 000 | Ai | 629 | 0x3A_StaStatus #115 , DA_Ai ,629 ,Ai ,629 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 124 | 124 | StaStatus #116 | Byte |  |  |  | 630 |  | Ditto | 000 | Ai | 630 | 0x3A_StaStatus #116 , DA_Ai ,630 ,Ai ,630 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 125 | 125 | StaStatus #117 | Byte |  |  |  | 631 |  | Ditto | 000 | Ai | 631 | 0x3A_StaStatus #117 , DA_Ai ,631 ,Ai ,631 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 126 | 126 | StaStatus #118 | Byte |  |  |  | 632 |  | Ditto | 000 | Ai | 632 | 0x3A_StaStatus #118 , DA_Ai ,632 ,Ai ,632 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 127 | 127 | StaStatus #119 | Byte |  |  |  | 633 |  | Ditto | 000 | Ai | 633 | 0x3A_StaStatus #119 , DA_Ai ,633 ,Ai ,633 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 128 | 128 | StaStatus #120 | Byte |  |  |  | 634 |  | Ditto | 000 | Ai | 634 | 0x3A_StaStatus #120 , DA_Ai ,634 ,Ai ,634 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 129 | 129 | StaStatus #121 | Byte |  |  |  | 635 |  | Ditto | 000 | Ai | 635 | 0x3A_StaStatus #121 , DA_Ai ,635 ,Ai ,635 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 130 | 130 | StaStatus #122 | Byte |  |  |  | 636 |  | Ditto | 000 | Ai | 636 | 0x3A_StaStatus #122 , DA_Ai ,636 ,Ai ,636 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 131 | 131 | StaStatus #123 | Byte |  |  |  | 637 |  | Ditto | 000 | Ai | 637 | 0x3A_StaStatus #123 , DA_Ai ,637 ,Ai ,637 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 132 | 132 | StaStatus #124 | Byte |  |  |  | 638 |  | Ditto | 000 | Ai | 638 | 0x3A_StaStatus #124 , DA_Ai ,638 ,Ai ,638 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 133 | 133 | StaStatus #125 | Byte |  |  |  | 639 |  | Ditto | 000 | Ai | 639 | 0x3A_StaStatus #125 , DA_Ai ,639 ,Ai ,639 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 134 | 134 | StaStatus #126 | Byte |  |  |  | 640 |  | Ditto | 000 | Ai | 640 | 0x3A_StaStatus #126 , DA_Ai ,640 ,Ai ,640 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 135 | 135 | StaStatus #127 | Byte |  |  |  | 641 |  | Ditto | 000 | Ai | 641 | 0x3A_StaStatus #127 , DA_Ai ,641 ,Ai ,641 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 136 | 136 | StaStatus #128 | Byte |  |  |  | 642 |  | Ditto | 000 | Ai | 642 | 0x3A_StaStatus #128 , DA_Ai ,642 ,Ai ,642 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 137 | 137 | StaStatus #129 | Byte |  |  |  | 643 |  | Ditto | 000 | Ai | 643 | 0x3A_StaStatus #129 , DA_Ai ,643 ,Ai ,643 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 138 | 138 | StaStatus #130 | Byte |  |  |  | 644 |  | Ditto | 000 | Ai | 644 | 0x3A_StaStatus #130 , DA_Ai ,644 ,Ai ,644 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 139 | 139 | StaStatus #131 | Byte |  |  |  | 645 |  | Ditto | 000 | Ai | 645 | 0x3A_StaStatus #131 , DA_Ai ,645 ,Ai ,645 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 140 | 140 | StaStatus #132 | Byte |  |  |  | 646 |  | Ditto | 000 | Ai | 646 | 0x3A_StaStatus #132 , DA_Ai ,646 ,Ai ,646 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 141 | 141 | StaStatus #133 | Byte |  |  |  | 647 |  | Ditto | 000 | Ai | 647 | 0x3A_StaStatus #133 , DA_Ai ,647 ,Ai ,647 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 142 | 142 | StaStatus #134 | Byte |  |  |  | 648 |  | Ditto | 000 | Ai | 648 | 0x3A_StaStatus #134 , DA_Ai ,648 ,Ai ,648 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 143 | 143 | StaStatus #135 | Byte |  |  |  | 649 |  | Ditto | 000 | Ai | 649 | 0x3A_StaStatus #135 , DA_Ai ,649 ,Ai ,649 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 144 | 144 | StaStatus #136 | Byte |  |  |  | 650 |  | Ditto | 000 | Ai | 650 | 0x3A_StaStatus #136 , DA_Ai ,650 ,Ai ,650 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 145 | 145 | StaStatus #137 | Byte |  |  |  | 651 |  | Ditto | 000 | Ai | 651 | 0x3A_StaStatus #137 , DA_Ai ,651 ,Ai ,651 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 146 | 146 | StaStatus #138 | Byte |  |  |  | 652 |  | Ditto | 000 | Ai | 652 | 0x3A_StaStatus #138 , DA_Ai ,652 ,Ai ,652 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 147 | 147 | StaStatus #139 | Byte |  |  |  | 653 |  | Ditto | 000 | Ai | 653 | 0x3A_StaStatus #139 , DA_Ai ,653 ,Ai ,653 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 148 | 148 | StaStatus #140 | Byte |  |  |  | 654 |  | Ditto | 000 | Ai | 654 | 0x3A_StaStatus #140 , DA_Ai ,654 ,Ai ,654 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 149 | 149 | StaStatus #141 | Byte |  |  |  | 655 |  | Ditto | 000 | Ai | 655 | 0x3A_StaStatus #141 , DA_Ai ,655 ,Ai ,655 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 150 | 150 | StaStatus #142 | Byte |  |  |  | 656 |  | Ditto | 000 | Ai | 656 | 0x3A_StaStatus #142 , DA_Ai ,656 ,Ai ,656 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 151 | 151 | StaStatus #143 | Byte |  |  |  | 657 |  | Ditto | 000 | Ai | 657 | 0x3A_StaStatus #143 , DA_Ai ,657 ,Ai ,657 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 152 | 152 | StaStatus #144 | Byte |  |  |  | 658 |  | Ditto | 000 | Ai | 658 | 0x3A_StaStatus #144 , DA_Ai ,658 ,Ai ,658 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 153 | 153 | StaStatus #145 | Byte |  |  |  | 659 |  | Ditto | 000 | Ai | 659 | 0x3A_StaStatus #145 , DA_Ai ,659 ,Ai ,659 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 154 | 154 | StaStatus #146 | Byte |  |  |  | 660 |  | Ditto | 000 | Ai | 660 | 0x3A_StaStatus #146 , DA_Ai ,660 ,Ai ,660 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 155 | 155 | StaStatus #147 | Byte |  |  |  | 661 |  | Ditto | 000 | Ai | 661 | 0x3A_StaStatus #147 , DA_Ai ,661 ,Ai ,661 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 156 | 156 | StaStatus #148 | Byte |  |  |  | 662 |  | Ditto | 000 | Ai | 662 | 0x3A_StaStatus #148 , DA_Ai ,662 ,Ai ,662 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 157 | 157 | StaStatus #149 | Byte |  |  |  | 663 |  | Ditto | 000 | Ai | 663 | 0x3A_StaStatus #149 , DA_Ai ,663 ,Ai ,663 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 158 | 158 | StaStatus #150 | Byte |  |  |  | 664 |  | Ditto | 000 | Ai | 664 | 0x3A_StaStatus #150 , DA_Ai ,664 ,Ai ,664 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 159 | 159 | StaStatus #151 | Byte |  |  |  | 665 |  | Ditto | 000 | Ai | 665 | 0x3A_StaStatus #151 , DA_Ai ,665 ,Ai ,665 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 160 | 160 | StaStatus #152 | Byte |  |  |  | 666 |  | Ditto | 000 | Ai | 666 | 0x3A_StaStatus #152 , DA_Ai ,666 ,Ai ,666 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 161 | 161 | StaStatus #153 | Byte |  |  |  | 667 |  | Ditto | 000 | Ai | 667 | 0x3A_StaStatus #153 , DA_Ai ,667 ,Ai ,667 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 162 | 162 | StaStatus #154 | Byte |  |  |  | 668 |  | Ditto | 000 | Ai | 668 | 0x3A_StaStatus #154 , DA_Ai ,668 ,Ai ,668 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 163 | 163 | StaStatus #155 | Byte |  |  |  | 669 |  | Ditto | 000 | Ai | 669 | 0x3A_StaStatus #155 , DA_Ai ,669 ,Ai ,669 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 164 | 164 | StaStatus #156 | Byte |  |  |  | 670 |  | Ditto | 000 | Ai | 670 | 0x3A_StaStatus #156 , DA_Ai ,670 ,Ai ,670 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 165 | 165 | StaStatus #157 | Byte |  |  |  | 671 |  | Ditto | 000 | Ai | 671 | 0x3A_StaStatus #157 , DA_Ai ,671 ,Ai ,671 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 166 | 166 | StaStatus #158 | Byte |  |  |  | 672 |  | Ditto | 000 | Ai | 672 | 0x3A_StaStatus #158 , DA_Ai ,672 ,Ai ,672 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 167 | 167 | StaStatus #159 | Byte |  |  |  | 673 |  | Ditto | 000 | Ai | 673 | 0x3A_StaStatus #159 , DA_Ai ,673 ,Ai ,673 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 168 | 168 | StaStatus #160 | Byte |  |  |  | 674 |  | Ditto | 000 | Ai | 674 | 0x3A_StaStatus #160 , DA_Ai ,674 ,Ai ,674 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 169 | 169 | StaStatus #161 | Byte |  |  |  | 675 |  | Ditto | 000 | Ai | 675 | 0x3A_StaStatus #161 , DA_Ai ,675 ,Ai ,675 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 170 | 170 | StaStatus #162 | Byte |  |  |  | 676 |  | Ditto | 000 | Ai | 676 | 0x3A_StaStatus #162 , DA_Ai ,676 ,Ai ,676 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 171 | 171 | StaStatus #163 | Byte |  |  |  | 677 |  | Ditto | 000 | Ai | 677 | 0x3A_StaStatus #163 , DA_Ai ,677 ,Ai ,677 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 172 | 172 | StaStatus #164 | Byte |  |  |  | 678 |  | Ditto | 000 | Ai | 678 | 0x3A_StaStatus #164 , DA_Ai ,678 ,Ai ,678 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 173 | 173 | StaStatus #165 | Byte |  |  |  | 679 |  | Ditto | 000 | Ai | 679 | 0x3A_StaStatus #165 , DA_Ai ,679 ,Ai ,679 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 174 | 174 | StaStatus #166 | Byte |  |  |  | 680 |  | Ditto | 000 | Ai | 680 | 0x3A_StaStatus #166 , DA_Ai ,680 ,Ai ,680 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 175 | 175 | StaStatus #167 | Byte |  |  |  | 681 |  | Ditto | 000 | Ai | 681 | 0x3A_StaStatus #167 , DA_Ai ,681 ,Ai ,681 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 176 | 176 | StaStatus #168 | Byte |  |  |  | 682 |  | Ditto | 000 | Ai | 682 | 0x3A_StaStatus #168 , DA_Ai ,682 ,Ai ,682 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 177 | 177 | StaStatus #169 | Byte |  |  |  | 683 |  | Ditto | 000 | Ai | 683 | 0x3A_StaStatus #169 , DA_Ai ,683 ,Ai ,683 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 178 | 178 | StaStatus #170 | Byte |  |  |  | 684 |  | Ditto | 000 | Ai | 684 | 0x3A_StaStatus #170 , DA_Ai ,684 ,Ai ,684 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 179 | 179 | StaStatus #171 | Byte |  |  |  | 685 |  | Ditto | 000 | Ai | 685 | 0x3A_StaStatus #171 , DA_Ai ,685 ,Ai ,685 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 180 | 180 | StaStatus #172 | Byte |  |  |  | 686 |  | Ditto | 000 | Ai | 686 | 0x3A_StaStatus #172 , DA_Ai ,686 ,Ai ,686 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 181 | 181 | StaStatus #173 | Byte |  |  |  | 687 |  | Ditto | 000 | Ai | 687 | 0x3A_StaStatus #173 , DA_Ai ,687 ,Ai ,687 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 182 | 182 | StaStatus #174 | Byte |  |  |  | 688 |  | Ditto | 000 | Ai | 688 | 0x3A_StaStatus #174 , DA_Ai ,688 ,Ai ,688 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 183 | 183 | StaStatus #175 | Byte |  |  |  | 689 |  | Ditto | 000 | Ai | 689 | 0x3A_StaStatus #175 , DA_Ai ,689 ,Ai ,689 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 184 | 184 | StaStatus #176 | Byte |  |  |  | 690 |  | Ditto | 000 | Ai | 690 | 0x3A_StaStatus #176 , DA_Ai ,690 ,Ai ,690 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 185 | 185 | StaStatus #177 | Byte |  |  |  | 691 |  | Ditto | 000 | Ai | 691 | 0x3A_StaStatus #177 , DA_Ai ,691 ,Ai ,691 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 186 | 186 | StaStatus #178 | Byte |  |  |  | 692 |  | Ditto | 000 | Ai | 692 | 0x3A_StaStatus #178 , DA_Ai ,692 ,Ai ,692 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 187 | 187 | StaStatus #179 | Byte |  |  |  | 693 |  | Ditto | 000 | Ai | 693 | 0x3A_StaStatus #179 , DA_Ai ,693 ,Ai ,693 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 188 | 188 | StaStatus #180 | Byte |  |  |  | 694 |  | Ditto | 000 | Ai | 694 | 0x3A_StaStatus #180 , DA_Ai ,694 ,Ai ,694 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 189 | 189 | StaStatus #181 | Byte |  |  |  | 695 |  | Ditto | 000 | Ai | 695 | 0x3A_StaStatus #181 , DA_Ai ,695 ,Ai ,695 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 190 | 190 | StaStatus #182 | Byte |  |  |  | 696 |  | Ditto | 000 | Ai | 696 | 0x3A_StaStatus #182 , DA_Ai ,696 ,Ai ,696 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 191 | 191 | StaStatus #183 | Byte |  |  |  | 697 |  | Ditto | 000 | Ai | 697 | 0x3A_StaStatus #183 , DA_Ai ,697 ,Ai ,697 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 192 | 192 | StaStatus #184 | Byte |  |  |  | 698 |  | Ditto | 000 | Ai | 698 | 0x3A_StaStatus #184 , DA_Ai ,698 ,Ai ,698 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 193 | 193 | StaStatus #185 | Byte |  |  |  | 699 |  | Ditto | 000 | Ai | 699 | 0x3A_StaStatus #185 , DA_Ai ,699 ,Ai ,699 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 194 | 194 | StaStatus #186 | Byte |  |  |  | 700 |  | Ditto | 000 | Ai | 700 | 0x3A_StaStatus #186 , DA_Ai ,700 ,Ai ,700 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 195 | 195 | StaStatus #187 | Byte |  |  |  | 701 |  | Ditto | 000 | Ai | 701 | 0x3A_StaStatus #187 , DA_Ai ,701 ,Ai ,701 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 196 | 196 | StaStatus #188 | Byte |  |  |  | 702 |  | Ditto | 000 | Ai | 702 | 0x3A_StaStatus #188 , DA_Ai ,702 ,Ai ,702 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 197 | 197 | StaStatus #189 | Byte |  |  |  | 703 |  | Ditto | 000 | Ai | 703 | 0x3A_StaStatus #189 , DA_Ai ,703 ,Ai ,703 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 198 | 198 | StaStatus #190 | Byte |  |  |  | 704 |  | Ditto | 000 | Ai | 704 | 0x3A_StaStatus #190 , DA_Ai ,704 ,Ai ,704 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 199 | 199 | StaStatus #191 | Byte |  |  |  | 705 |  | Ditto | 000 | Ai | 705 | 0x3A_StaStatus #191 , DA_Ai ,705 ,Ai ,705 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 200 | 200 | StaStatus #192 | Byte |  |  |  | 706 |  | Ditto | 000 | Ai | 706 | 0x3A_StaStatus #192 , DA_Ai ,706 ,Ai ,706 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 201 | 201 | StaStatus #193 | Byte |  |  |  | 707 |  | Ditto | 000 | Ai | 707 | 0x3A_StaStatus #193 , DA_Ai ,707 ,Ai ,707 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 202 | 202 | StaStatus #194 | Byte |  |  |  | 708 |  | Ditto | 000 | Ai | 708 | 0x3A_StaStatus #194 , DA_Ai ,708 ,Ai ,708 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 203 | 203 | StaStatus #195 | Byte |  |  |  | 709 |  | Ditto | 000 | Ai | 709 | 0x3A_StaStatus #195 , DA_Ai ,709 ,Ai ,709 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 204 | 204 | StaStatus #196 | Byte |  |  |  | 710 |  | Ditto | 000 | Ai | 710 | 0x3A_StaStatus #196 , DA_Ai ,710 ,Ai ,710 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 205 | 205 | StaStatus #197 | Byte |  |  |  | 711 |  | Ditto | 000 | Ai | 711 | 0x3A_StaStatus #197 , DA_Ai ,711 ,Ai ,711 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 206 | 206 | StaStatus #198 | Byte |  |  |  | 712 |  | Ditto | 000 | Ai | 712 | 0x3A_StaStatus #198 , DA_Ai ,712 ,Ai ,712 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 207 | 207 | StaStatus #199 | Byte |  |  |  | 713 |  | Ditto | 000 | Ai | 713 | 0x3A_StaStatus #199 , DA_Ai ,713 ,Ai ,713 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 208 | 208 | StaStatus #200 | Byte |  |  |  | 714 |  | Ditto | 000 | Ai | 714 | 0x3A_StaStatus #200 , DA_Ai ,714 ,Ai ,714 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 209 | 209 | StaStatus #201 | Byte |  |  |  | 715 |  | Ditto | 000 | Ai | 715 | 0x3A_StaStatus #201 , DA_Ai ,715 ,Ai ,715 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 210 | 210 | StaStatus #202 | Byte |  |  |  | 716 |  | Ditto | 000 | Ai | 716 | 0x3A_StaStatus #202 , DA_Ai ,716 ,Ai ,716 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 211 | 211 | StaStatus #203 | Byte |  |  |  | 717 |  | Ditto | 000 | Ai | 717 | 0x3A_StaStatus #203 , DA_Ai ,717 ,Ai ,717 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 212 | 212 | StaStatus #204 | Byte |  |  |  | 718 |  | Ditto | 000 | Ai | 718 | 0x3A_StaStatus #204 , DA_Ai ,718 ,Ai ,718 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 213 | 213 | StaStatus #205 | Byte |  |  |  | 719 |  | Ditto | 000 | Ai | 719 | 0x3A_StaStatus #205 , DA_Ai ,719 ,Ai ,719 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 214 | 214 | StaStatus #206 | Byte |  |  |  | 720 |  | Ditto | 000 | Ai | 720 | 0x3A_StaStatus #206 , DA_Ai ,720 ,Ai ,720 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 215 | 215 | StaStatus #207 | Byte |  |  |  | 721 |  | Ditto | 000 | Ai | 721 | 0x3A_StaStatus #207 , DA_Ai ,721 ,Ai ,721 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 216 | 216 | StaStatus #208 | Byte |  |  |  | 722 |  | Ditto | 000 | Ai | 722 | 0x3A_StaStatus #208 , DA_Ai ,722 ,Ai ,722 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 217 | 217 | StaStatus #209 | Byte |  |  |  | 723 |  | Ditto | 000 | Ai | 723 | 0x3A_StaStatus #209 , DA_Ai ,723 ,Ai ,723 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 218 | 218 | StaStatus #210 | Byte |  |  |  | 724 |  | Ditto | 000 | Ai | 724 | 0x3A_StaStatus #210 , DA_Ai ,724 ,Ai ,724 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 219 | 219 | StaStatus #211 | Byte |  |  |  | 725 |  | Ditto | 000 | Ai | 725 | 0x3A_StaStatus #211 , DA_Ai ,725 ,Ai ,725 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 220 | 220 | StaStatus #212 | Byte |  |  |  | 726 |  | Ditto | 000 | Ai | 726 | 0x3A_StaStatus #212 , DA_Ai ,726 ,Ai ,726 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 221 | 221 | StaStatus #213 | Byte |  |  |  | 727 |  | Ditto | 000 | Ai | 727 | 0x3A_StaStatus #213 , DA_Ai ,727 ,Ai ,727 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 222 | 222 | StaStatus #214 | Byte |  |  |  | 728 |  | Ditto | 000 | Ai | 728 | 0x3A_StaStatus #214 , DA_Ai ,728 ,Ai ,728 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 223 | 223 | StaStatus #215 | Byte |  |  |  | 729 |  | Ditto | 000 | Ai | 729 | 0x3A_StaStatus #215 , DA_Ai ,729 ,Ai ,729 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 224 | 224 | StaStatus #216 | Byte |  |  |  | 730 |  | Ditto | 000 | Ai | 730 | 0x3A_StaStatus #216 , DA_Ai ,730 ,Ai ,730 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 225 | 225 | StaStatus #217 | Byte |  |  |  | 731 |  | Ditto | 000 | Ai | 731 | 0x3A_StaStatus #217 , DA_Ai ,731 ,Ai ,731 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 226 | 226 | StaStatus #218 | Byte |  |  |  | 732 |  | Ditto | 000 | Ai | 732 | 0x3A_StaStatus #218 , DA_Ai ,732 ,Ai ,732 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 227 | 227 | StaStatus #219 | Byte |  |  |  | 733 |  | Ditto | 000 | Ai | 733 | 0x3A_StaStatus #219 , DA_Ai ,733 ,Ai ,733 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 228 | 228 | StaStatus #220 | Byte |  |  |  | 734 |  | Ditto | 000 | Ai | 734 | 0x3A_StaStatus #220 , DA_Ai ,734 ,Ai ,734 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 229 | 229 | StaStatus #221 | Byte |  |  |  | 735 |  | Ditto | 000 | Ai | 735 | 0x3A_StaStatus #221 , DA_Ai ,735 ,Ai ,735 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 230 | 230 | StaStatus #222 | Byte |  |  |  | 736 |  | Ditto | 000 | Ai | 736 | 0x3A_StaStatus #222 , DA_Ai ,736 ,Ai ,736 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 231 | 231 | StaStatus #223 | Byte |  |  |  | 737 |  | Ditto | 000 | Ai | 737 | 0x3A_StaStatus #223 , DA_Ai ,737 ,Ai ,737 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
0x3A | 232 | 233 | StaStatus #225 | Byte |  |  |  | 740 |  | Ditto | 000 | Ai | 740 | 0x3A_StaStatus #225 , DA_Ai ,740 ,Ai ,740 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Ditto ,
000
000
000
0x3B – REPORT FLOW SENSOR PARAMETERS (v2.00.033 and Later) | [10 empty] | 000 |  |  |  |  | 0x3B – REPORT FLOW SENSOR PARAMETERS (v2.00.033 and Later)
| demo=h1b.html | [9 empty] | 000
| template=Type1 | [9 empty] | 000
| Sister Service = 0x1B | [9 empty] | 000
| This command reports the sensor settings for each of the six flow sensors in the controller. It includes the location, type of sensor installed, and the sensor configuration. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x3B | 0 | 1 | Type | Byte |  |  |  | 741 | FlowSen1 | Type of Flow Sensor being used. | 000 | Ai | 741 | 0x3B_FlowSen1Type , DA_Ai ,741 ,Ai ,741 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x3B | 1 | 2 | Location | Byte |  |  |  | 742 | FlowSen1 | Location of the Sensor. | 000 | Ai | 742 | 0x3B_FlowSen1Location , DA_Ai ,742 ,Ai ,742 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. ,
0x3B | 2 | 3 | DecMod | Byte |  |  |  | 743 | FlowSen1 | Decoder Module number responsible for the sensors. Value should be ignored if Location is Fixed. Range is 1 to 3. | 000 | Ai | 743 | 0x3B_FlowSen1DecMod , DA_Ai ,743 ,Ai ,743 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module number responsible for t ,
0x3B | 3 | 4 | DecAdd | Byte |  |  |  | 744 | FlowSen1 | Sensor Decoder Address. Value should be ignored if Location is Fixed. Range is 1 to 9. | 000 | Ai | 744 | 0x3B_FlowSen1DecAdd , DA_Ai ,744 ,Ai ,744 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address. Value should be ,
0x3B | 4 | 5 | Kfactor | UINT32 |  |  |  | 745 | FlowSen1 | K-Factor of the Flow Sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 representing actual values of 0.0001 to 999.9999. | 000 | Ai | 745 | 0x3B_FlowSen1Kfactor , DA_Ai ,745 ,Ai ,745 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor times 10-00 ,
0x3B | 5 | 6 | Offset | UINT32 |  |  |  | 746 | FlowSen1 | Offset of the Flow sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Ai | 746 | 0x3B_FlowSen1Offset , DA_Ai ,746 ,Ai ,746 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x3B | 6 | 7 | GalPerPulse | UINT32 |  |  |  | 747 | FlowSen1 | Rate per pulse times 10-000 (Gallongs or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Ai | 747 | 0x3B_FlowSen1GalPerPulse , DA_Ai ,747 ,Ai ,747 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Gallongs o ,
0x3B | 7 | 8 | PulseUnits | Byte |  |  |  | 748 | FlowSen1 | Units or the Pulse Rate. Range is 0 to 1. 0 = Gallons 1 = Liters | 000 | Ai | 748 | 0x3B_FlowSen1PulseUnits , DA_Ai ,748 ,Ai ,748 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units or the Pulse Rate. Range is 0 to ,
0x3B | 8 | 9 | Wireless | Byte |  |  |  | 749 | FlowSen1 | Is wireless or not. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless 1 = Wireless | 000 | Ai | 749 | 0x3B_FlowSen1Wireless , DA_Ai ,749 ,Ai ,749 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Is wireless or not. Only applies to Hu ,
0x3B | 9 | 10 | Type | Byte |  |  |  | 750 | FlowSen2 | Type of Flow Sensor being used. | 000 | Ai | 750 | 0x3B_FlowSen2Type , DA_Ai ,750 ,Ai ,750 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x3B | 10 | 11 | Location | Byte |  |  |  | 751 | FlowSen2 | Location of the Sensor. | 000 | Ai | 751 | 0x3B_FlowSen2Location , DA_Ai ,751 ,Ai ,751 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. ,
0x3B | 11 | 12 | DecMod | Byte |  |  |  | 752 | FlowSen2 | Decoder Module number responsible for the sensors. Value should be ignored if Location is Fixed. Range is 1 to 3. | 000 | Ai | 752 | 0x3B_FlowSen2DecMod , DA_Ai ,752 ,Ai ,752 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module number responsible for t ,
0x3B | 12 | 13 | DecAdd | Byte |  |  |  | 753 | FlowSen2 | Sensor Decoder Address. Value should be ignored if Location is Fixed. Range is 1 to 9. | 000 | Ai | 753 | 0x3B_FlowSen2DecAdd , DA_Ai ,753 ,Ai ,753 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address. Value should be ,
0x3B | 13 | 14 | Kfactor | UINT32 |  |  |  | 754 | FlowSen2 | K-Factor of the Flow Sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 representing actual values of 0.0001 to 999.9999. | 000 | Ai | 754 | 0x3B_FlowSen2Kfactor , DA_Ai ,754 ,Ai ,754 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor times 10-00 ,
0x3B | 14 | 15 | Offset | UINT32 |  |  |  | 755 | FlowSen2 | Offset of the Flow sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Ai | 755 | 0x3B_FlowSen2Offset , DA_Ai ,755 ,Ai ,755 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x3B | 15 | 16 | GalPerPulse | UINT32 |  |  |  | 756 | FlowSen2 | Rate per pulse times 10-000 (Gallongs or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Ai | 756 | 0x3B_FlowSen2GalPerPulse , DA_Ai ,756 ,Ai ,756 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Gallongs o ,
0x3B | 16 | 17 | PulseUnits | Byte |  |  |  | 757 | FlowSen2 | Units or the Pulse Rate. Range is 0 to 1. 0 = Gallons 1 = Liters | 000 | Ai | 757 | 0x3B_FlowSen2PulseUnits , DA_Ai ,757 ,Ai ,757 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units or the Pulse Rate. Range is 0 to ,
0x3B | 17 | 18 | Wireless | Byte |  |  |  | 758 | FlowSen2 | Is wireless or not. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless 1 = Wireless | 000 | Ai | 758 | 0x3B_FlowSen2Wireless , DA_Ai ,758 ,Ai ,758 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Is wireless or not. Only applies to Hu ,
0x3B | 18 | 19 | Type | Byte |  |  |  | 759 | FlowSen3 | Type of Flow Sensor being used. | 000 | Ai | 759 | 0x3B_FlowSen3Type , DA_Ai ,759 ,Ai ,759 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x3B | 19 | 20 | Location | Byte |  |  |  | 760 | FlowSen3 | Location of the Sensor. | 000 | Ai | 760 | 0x3B_FlowSen3Location , DA_Ai ,760 ,Ai ,760 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. ,
0x3B | 20 | 21 | DecMod | Byte |  |  |  | 761 | FlowSen3 | Decoder Module number responsible for the sensors. Value should be ignored if Location is Fixed. Range is 1 to 3. | 000 | Ai | 761 | 0x3B_FlowSen3DecMod , DA_Ai ,761 ,Ai ,761 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module number responsible for t ,
0x3B | 21 | 22 | DecAdd | Byte |  |  |  | 762 | FlowSen3 | Sensor Decoder Address. Value should be ignored if Location is Fixed. Range is 1 to 9. | 000 | Ai | 762 | 0x3B_FlowSen3DecAdd , DA_Ai ,762 ,Ai ,762 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address. Value should be ,
0x3B | 22 | 23 | Kfactor | UINT32 |  |  |  | 763 | FlowSen3 | K-Factor of the Flow Sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 representing actual values of 0.0001 to 999.9999. | 000 | Ai | 763 | 0x3B_FlowSen3Kfactor , DA_Ai ,763 ,Ai ,763 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor times 10-00 ,
0x3B | 23 | 24 | Offset | UINT32 |  |  |  | 764 | FlowSen3 | Offset of the Flow sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Ai | 764 | 0x3B_FlowSen3Offset , DA_Ai ,764 ,Ai ,764 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x3B | 24 | 25 | GalPerPulse | UINT32 |  |  |  | 765 | FlowSen3 | Rate per pulse times 10-000 (Gallongs or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Ai | 765 | 0x3B_FlowSen3GalPerPulse , DA_Ai ,765 ,Ai ,765 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Gallongs o ,
0x3B | 25 | 26 | PulseUnits | Byte |  |  |  | 766 | FlowSen3 | Units or the Pulse Rate. Range is 0 to 1. 0 = Gallons 1 = Liters | 000 | Ai | 766 | 0x3B_FlowSen3PulseUnits , DA_Ai ,766 ,Ai ,766 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units or the Pulse Rate. Range is 0 to ,
0x3B | 26 | 27 | Wireless | Byte |  |  |  | 767 | FlowSen3 | Is wireless or not. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless 1 = Wireless | 000 | Ai | 767 | 0x3B_FlowSen3Wireless , DA_Ai ,767 ,Ai ,767 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Is wireless or not. Only applies to Hu ,
0x3B | 27 | 28 | Type | Byte |  |  |  | 768 | FlowSen4 | Type of Flow Sensor being used. | 000 | Ai | 768 | 0x3B_FlowSen4Type , DA_Ai ,768 ,Ai ,768 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x3B | 28 | 29 | Location | Byte |  |  |  | 769 | FlowSen4 | Location of the Sensor. | 000 | Ai | 769 | 0x3B_FlowSen4Location , DA_Ai ,769 ,Ai ,769 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. ,
0x3B | 29 | 30 | DecMod | Byte |  |  |  | 770 | FlowSen4 | Decoder Module number responsible for the sensors. Value should be ignored if Location is Fixed. Range is 1 to 3. | 000 | Ai | 770 | 0x3B_FlowSen4DecMod , DA_Ai ,770 ,Ai ,770 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module number responsible for t ,
0x3B | 30 | 31 | DecAdd | Byte |  |  |  | 771 | FlowSen4 | Sensor Decoder Address. Value should be ignored if Location is Fixed. Range is 1 to 9. | 000 | Ai | 771 | 0x3B_FlowSen4DecAdd , DA_Ai ,771 ,Ai ,771 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address. Value should be ,
0x3B | 31 | 32 | Kfactor | UINT32 |  |  |  | 772 | FlowSen4 | K-Factor of the Flow Sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 representing actual values of 0.0001 to 999.9999. | 000 | Ai | 772 | 0x3B_FlowSen4Kfactor , DA_Ai ,772 ,Ai ,772 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor times 10-00 ,
0x3B | 32 | 33 | Offset | UINT32 |  |  |  | 773 | FlowSen4 | Offset of the Flow sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Ai | 773 | 0x3B_FlowSen4Offset , DA_Ai ,773 ,Ai ,773 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x3B | 33 | 34 | GalPerPulse | UINT32 |  |  |  | 774 | FlowSen4 | Rate per pulse times 10-000 (Gallongs or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Ai | 774 | 0x3B_FlowSen4GalPerPulse , DA_Ai ,774 ,Ai ,774 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Gallongs o ,
0x3B | 34 | 35 | PulseUnits | Byte |  |  |  | 775 | FlowSen4 | Units or the Pulse Rate. Range is 0 to 1. 0 = Gallons 1 = Liters | 000 | Ai | 775 | 0x3B_FlowSen4PulseUnits , DA_Ai ,775 ,Ai ,775 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units or the Pulse Rate. Range is 0 to ,
0x3B | 35 | 36 | Wireless | Byte |  |  |  | 776 | FlowSen4 | Is wireless or not. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless 1 = Wireless | 000 | Ai | 776 | 0x3B_FlowSen4Wireless , DA_Ai ,776 ,Ai ,776 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Is wireless or not. Only applies to Hu ,
0x3B | 36 | 37 | Type | Byte |  |  |  | 777 | FlowSen5 | Type of Flow Sensor being used. | 000 | Ai | 777 | 0x3B_FlowSen5Type , DA_Ai ,777 ,Ai ,777 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x3B | 37 | 38 | Location | Byte |  |  |  | 778 | FlowSen5 | Location of the Sensor. | 000 | Ai | 778 | 0x3B_FlowSen5Location , DA_Ai ,778 ,Ai ,778 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. ,
0x3B | 38 | 39 | DecMod | Byte |  |  |  | 779 | FlowSen5 | Decoder Module number responsible for the sensors. Value should be ignored if Location is Fixed. Range is 1 to 3. | 000 | Ai | 779 | 0x3B_FlowSen5DecMod , DA_Ai ,779 ,Ai ,779 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module number responsible for t ,
0x3B | 39 | 40 | DecAdd | Byte |  |  |  | 780 | FlowSen5 | Sensor Decoder Address. Value should be ignored if Location is Fixed. Range is 1 to 9. | 000 | Ai | 780 | 0x3B_FlowSen5DecAdd , DA_Ai ,780 ,Ai ,780 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address. Value should be ,
0x3B | 40 | 41 | Kfactor | UINT32 |  |  |  | 781 | FlowSen5 | K-Factor of the Flow Sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 representing actual values of 0.0001 to 999.9999. | 000 | Ai | 781 | 0x3B_FlowSen5Kfactor , DA_Ai ,781 ,Ai ,781 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor times 10-00 ,
0x3B | 41 | 42 | Offset | UINT32 |  |  |  | 782 | FlowSen5 | Offset of the Flow sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Ai | 782 | 0x3B_FlowSen5Offset , DA_Ai ,782 ,Ai ,782 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x3B | 42 | 43 | GalPerPulse | UINT32 |  |  |  | 783 | FlowSen5 | Rate per pulse times 10-000 (Gallongs or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Ai | 783 | 0x3B_FlowSen5GalPerPulse , DA_Ai ,783 ,Ai ,783 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Gallongs o ,
0x3B | 43 | 44 | PulseUnits | Byte |  |  |  | 784 | FlowSen5 | Units or the Pulse Rate. Range is 0 to 1. 0 = Gallons 1 = Liters | 000 | Ai | 784 | 0x3B_FlowSen5PulseUnits , DA_Ai ,784 ,Ai ,784 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units or the Pulse Rate. Range is 0 to ,
0x3B | 44 | 45 | Wireless | Byte |  |  |  | 785 | FlowSen5 | Is wireless or not. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless 1 = Wireless | 000 | Ai | 785 | 0x3B_FlowSen5Wireless , DA_Ai ,785 ,Ai ,785 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Is wireless or not. Only applies to Hu ,
0x3B | 45 | 46 | Type | Byte |  |  |  | 786 | FlowSen6 | Type of Flow Sensor being used. | 000 | Ai | 786 | 0x3B_FlowSen6Type , DA_Ai ,786 ,Ai ,786 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Type of Flow Sensor being used. ,
0x3B | 46 | 47 | Location | Byte |  |  |  | 787 | FlowSen6 | Location of the Sensor. | 000 | Ai | 787 | 0x3B_FlowSen6Location , DA_Ai ,787 ,Ai ,787 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Location of the Sensor. ,
0x3B | 47 | 48 | DecMod | Byte |  |  |  | 788 | FlowSen6 | Decoder Module number responsible for the sensors. Value should be ignored if Location is Fixed. Range is 1 to 3. | 000 | Ai | 788 | 0x3B_FlowSen6DecMod , DA_Ai ,788 ,Ai ,788 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module number responsible for t ,
0x3B | 48 | 49 | DecAdd | Byte |  |  |  | 789 | FlowSen6 | Sensor Decoder Address. Value should be ignored if Location is Fixed. Range is 1 to 9. | 000 | Ai | 789 | 0x3B_FlowSen6DecAdd , DA_Ai ,789 ,Ai ,789 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Sensor Decoder Address. Value should be ,
0x3B | 49 | 50 | Kfactor | UINT32 |  |  |  | 790 | FlowSen6 | K-Factor of the Flow Sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is 1 to 9-999-999 representing actual values of 0.0001 to 999.9999. | 000 | Ai | 790 | 0x3B_FlowSen6Kfactor , DA_Ai ,790 ,Ai ,790 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,K-Factor of the Flow Sensor times 10-00 ,
0x3B | 50 | 51 | Offset | UINT32 |  |  |  | 791 | FlowSen6 | Offset of the Flow sensor times 10-000. Value should be ignored if Type is not Other (K-Factor + Offset). Range is -999-999 to 999-999 representing actual values of -99.9999 to 99.9999. | 000 | Ai | 791 | 0x3B_FlowSen6Offset , DA_Ai ,791 ,Ai ,791 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Offset of the Flow sensor times 10-000. ,
0x3B | 51 | 52 | GalPerPulse | UINT32 |  |  |  | 792 | FlowSen6 | Rate per pulse times 10-000 (Gallongs or Liters depending on PulseUnits value). Value is ignored if Type is not Other (Pulses Rate). Range is 1 to 10-000-00 representing actual values 0.0001 to 1000.0000. | 000 | Ai | 792 | 0x3B_FlowSen6GalPerPulse , DA_Ai ,792 ,Ai ,792 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Rate per pulse times 10-000 (Gallongs o ,
0x3B | 52 | 53 | PulseUnits | Byte |  |  |  | 793 | FlowSen6 | Units or the Pulse Rate. Range is 0 to 1. 0 = Gallons 1 = Liters | 000 | Ai | 793 | 0x3B_FlowSen6PulseUnits , DA_Ai ,793 ,Ai ,793 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Units or the Pulse Rate. Range is 0 to ,
0x3B | 53 | 54 | Wireless | Byte |  |  |  | 794 | FlowSen6 | Is wireless or not. Only applies to Hunter Flow Sensors (HFS FCTxxx). Range is 0 to 1. 0 = NOT Wireless 1 = Wireless | 000 | Ai | 794 | 0x3B_FlowSen6Wireless , DA_Ai ,794 ,Ai ,794 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Is wireless or not. Only applies to Hu ,
000
0x3C – REPORT CLICK SENSOR PARAMETERS | [10 empty] | 000 |  |  |  |  | 0x3C – REPORT CLICK SENSOR PARAMETERS
| This command reports the Clik Sensor Parameters of the three Clik Sensors of the controller. It includes the type of sensor installed and its location. | [9 empty] | 000
| Not Implememented | [9 empty] | 000
000
0x3D – REPORT PROGRAM SENSOR ACTION | [10 empty] | 000 |  |  |  |  | 0x3D – REPORT PROGRAM SENSOR ACTION
| demo=h3d.html | [9 empty] | 000
| template=Type2 | [9 empty] | 000
| sister service = 0x1D | [9 empty] | 000
| This command reports the Program action for each of the switch type Sensors of the Controller to take when the Sensor is active. Sensors supported include the Clik Sensors and Solar Sync Sensor. All Programs will be reported in the response. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x3D | 1 | 1 | ProgramNum | Byte |  |  |  | 795 | Prgm 1 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 795 | 0x3D_Prgm 1ProgramNum , DA_Ai ,795 ,Ai ,795 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 2 | 2 | Clik1Action | Byte |  |  |  | 796 | Prgm 1 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 796 | 0x3D_Prgm 1Clik1Action , DA_Ai ,796 ,Ai ,796 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 3 | 3 | Clik2Action | Byte |  |  |  | 797 | Prgm 1 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 797 | 0x3D_Prgm 1Clik2Action , DA_Ai ,797 ,Ai ,797 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 4 | 4 | Clik3Action | Byte |  |  |  | 798 | Prgm 1 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 798 | 0x3D_Prgm 1Clik3Action , DA_Ai ,798 ,Ai ,798 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 5 | 5 | SSRainAction | Byte |  |  |  | 799 | Prgm 1 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 799 | 0x3D_Prgm 1SSRainAction , DA_Ai ,799 ,Ai ,799 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 6 | 6 | SSFreezeAction | Byte |  |  |  | 800 | Prgm 1 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 800 | 0x3D_Prgm 1SSFreezeAction , DA_Ai ,800 ,Ai ,800 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 7 | 7 | ProgramNum | Byte |  |  |  | 801 | Prgm 2 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 801 | 0x3D_Prgm 2ProgramNum , DA_Ai ,801 ,Ai ,801 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 8 | 8 | Clik1Action | Byte |  |  |  | 802 | Prgm 2 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 802 | 0x3D_Prgm 2Clik1Action , DA_Ai ,802 ,Ai ,802 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 9 | 9 | Clik2Action | Byte |  |  |  | 803 | Prgm 2 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 803 | 0x3D_Prgm 2Clik2Action , DA_Ai ,803 ,Ai ,803 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 10 | 10 | Clik3Action | Byte |  |  |  | 804 | Prgm 2 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 804 | 0x3D_Prgm 2Clik3Action , DA_Ai ,804 ,Ai ,804 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 11 | 11 | SSRainAction | Byte |  |  |  | 805 | Prgm 2 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 805 | 0x3D_Prgm 2SSRainAction , DA_Ai ,805 ,Ai ,805 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 12 | 12 | SSFreezeAction | Byte |  |  |  | 806 | Prgm 2 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 806 | 0x3D_Prgm 2SSFreezeAction , DA_Ai ,806 ,Ai ,806 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 13 | 13 | ProgramNum | Byte |  |  |  | 807 | Prgm 3 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 807 | 0x3D_Prgm 3ProgramNum , DA_Ai ,807 ,Ai ,807 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 14 | 14 | Clik1Action | Byte |  |  |  | 808 | Prgm 3 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 808 | 0x3D_Prgm 3Clik1Action , DA_Ai ,808 ,Ai ,808 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 15 | 15 | Clik2Action | Byte |  |  |  | 809 | Prgm 3 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 809 | 0x3D_Prgm 3Clik2Action , DA_Ai ,809 ,Ai ,809 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 16 | 16 | Clik3Action | Byte |  |  |  | 810 | Prgm 3 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 810 | 0x3D_Prgm 3Clik3Action , DA_Ai ,810 ,Ai ,810 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 17 | 17 | SSRainAction | Byte |  |  |  | 811 | Prgm 3 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 811 | 0x3D_Prgm 3SSRainAction , DA_Ai ,811 ,Ai ,811 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 18 | 18 | SSFreezeAction | Byte |  |  |  | 812 | Prgm 3 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 812 | 0x3D_Prgm 3SSFreezeAction , DA_Ai ,812 ,Ai ,812 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 19 | 19 | ProgramNum | Byte |  |  |  | 813 | Prgm 4 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 813 | 0x3D_Prgm 4ProgramNum , DA_Ai ,813 ,Ai ,813 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 20 | 20 | Clik1Action | Byte |  |  |  | 814 | Prgm 4 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 814 | 0x3D_Prgm 4Clik1Action , DA_Ai ,814 ,Ai ,814 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 21 | 21 | Clik2Action | Byte |  |  |  | 815 | Prgm 4 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 815 | 0x3D_Prgm 4Clik2Action , DA_Ai ,815 ,Ai ,815 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 22 | 22 | Clik3Action | Byte |  |  |  | 816 | Prgm 4 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 816 | 0x3D_Prgm 4Clik3Action , DA_Ai ,816 ,Ai ,816 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 23 | 23 | SSRainAction | Byte |  |  |  | 817 | Prgm 4 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 817 | 0x3D_Prgm 4SSRainAction , DA_Ai ,817 ,Ai ,817 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 24 | 24 | SSFreezeAction | Byte |  |  |  | 818 | Prgm 4 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 818 | 0x3D_Prgm 4SSFreezeAction , DA_Ai ,818 ,Ai ,818 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 25 | 25 | ProgramNum | Byte |  |  |  | 819 | Prgm 5 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 819 | 0x3D_Prgm 5ProgramNum , DA_Ai ,819 ,Ai ,819 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 26 | 26 | Clik1Action | Byte |  |  |  | 820 | Prgm 5 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 820 | 0x3D_Prgm 5Clik1Action , DA_Ai ,820 ,Ai ,820 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 27 | 27 | Clik2Action | Byte |  |  |  | 821 | Prgm 5 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 821 | 0x3D_Prgm 5Clik2Action , DA_Ai ,821 ,Ai ,821 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 28 | 28 | Clik3Action | Byte |  |  |  | 822 | Prgm 5 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 822 | 0x3D_Prgm 5Clik3Action , DA_Ai ,822 ,Ai ,822 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 29 | 29 | SSRainAction | Byte |  |  |  | 823 | Prgm 5 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 823 | 0x3D_Prgm 5SSRainAction , DA_Ai ,823 ,Ai ,823 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 30 | 30 | SSFreezeAction | Byte |  |  |  | 824 | Prgm 5 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 824 | 0x3D_Prgm 5SSFreezeAction , DA_Ai ,824 ,Ai ,824 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 31 | 31 | ProgramNum | Byte |  |  |  | 825 | Prgm 6 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 825 | 0x3D_Prgm 6ProgramNum , DA_Ai ,825 ,Ai ,825 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 32 | 32 | Clik1Action | Byte |  |  |  | 826 | Prgm 6 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 826 | 0x3D_Prgm 6Clik1Action , DA_Ai ,826 ,Ai ,826 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 33 | 33 | Clik2Action | Byte |  |  |  | 827 | Prgm 6 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 827 | 0x3D_Prgm 6Clik2Action , DA_Ai ,827 ,Ai ,827 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 34 | 34 | Clik3Action | Byte |  |  |  | 828 | Prgm 6 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 828 | 0x3D_Prgm 6Clik3Action , DA_Ai ,828 ,Ai ,828 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 35 | 35 | SSRainAction | Byte |  |  |  | 829 | Prgm 6 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 829 | 0x3D_Prgm 6SSRainAction , DA_Ai ,829 ,Ai ,829 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 36 | 36 | SSFreezeAction | Byte |  |  |  | 830 | Prgm 6 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 830 | 0x3D_Prgm 6SSFreezeAction , DA_Ai ,830 ,Ai ,830 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 37 | 37 | ProgramNum | Byte |  |  |  | 831 | Prgm 7 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 831 | 0x3D_Prgm 7ProgramNum , DA_Ai ,831 ,Ai ,831 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 38 | 38 | Clik1Action | Byte |  |  |  | 832 | Prgm 7 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 832 | 0x3D_Prgm 7Clik1Action , DA_Ai ,832 ,Ai ,832 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 39 | 39 | Clik2Action | Byte |  |  |  | 833 | Prgm 7 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 833 | 0x3D_Prgm 7Clik2Action , DA_Ai ,833 ,Ai ,833 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 40 | 40 | Clik3Action | Byte |  |  |  | 834 | Prgm 7 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 834 | 0x3D_Prgm 7Clik3Action , DA_Ai ,834 ,Ai ,834 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 41 | 41 | SSRainAction | Byte |  |  |  | 835 | Prgm 7 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 835 | 0x3D_Prgm 7SSRainAction , DA_Ai ,835 ,Ai ,835 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 42 | 42 | SSFreezeAction | Byte |  |  |  | 836 | Prgm 7 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 836 | 0x3D_Prgm 7SSFreezeAction , DA_Ai ,836 ,Ai ,836 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 43 | 43 | ProgramNum | Byte |  |  |  | 837 | Prgm 8 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 837 | 0x3D_Prgm 8ProgramNum , DA_Ai ,837 ,Ai ,837 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 44 | 44 | Clik1Action | Byte |  |  |  | 838 | Prgm 8 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 838 | 0x3D_Prgm 8Clik1Action , DA_Ai ,838 ,Ai ,838 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 45 | 45 | Clik2Action | Byte |  |  |  | 839 | Prgm 8 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 839 | 0x3D_Prgm 8Clik2Action , DA_Ai ,839 ,Ai ,839 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 46 | 46 | Clik3Action | Byte |  |  |  | 840 | Prgm 8 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 840 | 0x3D_Prgm 8Clik3Action , DA_Ai ,840 ,Ai ,840 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 47 | 47 | SSRainAction | Byte |  |  |  | 841 | Prgm 8 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 841 | 0x3D_Prgm 8SSRainAction , DA_Ai ,841 ,Ai ,841 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 48 | 48 | SSFreezeAction | Byte |  |  |  | 842 | Prgm 8 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 842 | 0x3D_Prgm 8SSFreezeAction , DA_Ai ,842 ,Ai ,842 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 49 | 49 | ProgramNum | Byte |  |  |  | 843 | Prgm 9 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 843 | 0x3D_Prgm 9ProgramNum , DA_Ai ,843 ,Ai ,843 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 50 | 50 | Clik1Action | Byte |  |  |  | 844 | Prgm 9 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 844 | 0x3D_Prgm 9Clik1Action , DA_Ai ,844 ,Ai ,844 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 51 | 51 | Clik2Action | Byte |  |  |  | 845 | Prgm 9 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 845 | 0x3D_Prgm 9Clik2Action , DA_Ai ,845 ,Ai ,845 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 52 | 52 | Clik3Action | Byte |  |  |  | 846 | Prgm 9 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 846 | 0x3D_Prgm 9Clik3Action , DA_Ai ,846 ,Ai ,846 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 53 | 53 | SSRainAction | Byte |  |  |  | 847 | Prgm 9 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 847 | 0x3D_Prgm 9SSRainAction , DA_Ai ,847 ,Ai ,847 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 54 | 54 | SSFreezeAction | Byte |  |  |  | 848 | Prgm 9 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 848 | 0x3D_Prgm 9SSFreezeAction , DA_Ai ,848 ,Ai ,848 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 55 | 55 | ProgramNum | Byte |  |  |  | 849 | Prgm 10 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 849 | 0x3D_Prgm 10ProgramNum , DA_Ai ,849 ,Ai ,849 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 56 | 56 | Clik1Action | Byte |  |  |  | 850 | Prgm 10 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 850 | 0x3D_Prgm 10Clik1Action , DA_Ai ,850 ,Ai ,850 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 57 | 57 | Clik2Action | Byte |  |  |  | 851 | Prgm 10 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 851 | 0x3D_Prgm 10Clik2Action , DA_Ai ,851 ,Ai ,851 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 58 | 58 | Clik3Action | Byte |  |  |  | 852 | Prgm 10 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 852 | 0x3D_Prgm 10Clik3Action , DA_Ai ,852 ,Ai ,852 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 59 | 59 | SSRainAction | Byte |  |  |  | 853 | Prgm 10 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 853 | 0x3D_Prgm 10SSRainAction , DA_Ai ,853 ,Ai ,853 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 60 | 60 | SSFreezeAction | Byte |  |  |  | 854 | Prgm 10 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 854 | 0x3D_Prgm 10SSFreezeAction , DA_Ai ,854 ,Ai ,854 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 61 | 61 | ProgramNum | Byte |  |  |  | 855 | Prgm 11 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 855 | 0x3D_Prgm 11ProgramNum , DA_Ai ,855 ,Ai ,855 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 62 | 62 | Clik1Action | Byte |  |  |  | 856 | Prgm 11 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 856 | 0x3D_Prgm 11Clik1Action , DA_Ai ,856 ,Ai ,856 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 63 | 63 | Clik2Action | Byte |  |  |  | 857 | Prgm 11 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 857 | 0x3D_Prgm 11Clik2Action , DA_Ai ,857 ,Ai ,857 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 64 | 64 | Clik3Action | Byte |  |  |  | 858 | Prgm 11 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 858 | 0x3D_Prgm 11Clik3Action , DA_Ai ,858 ,Ai ,858 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 65 | 65 | SSRainAction | Byte |  |  |  | 859 | Prgm 11 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 859 | 0x3D_Prgm 11SSRainAction , DA_Ai ,859 ,Ai ,859 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 66 | 66 | SSFreezeAction | Byte |  |  |  | 860 | Prgm 11 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 860 | 0x3D_Prgm 11SSFreezeAction , DA_Ai ,860 ,Ai ,860 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 67 | 67 | ProgramNum | Byte |  |  |  | 861 | Prgm 12 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 861 | 0x3D_Prgm 12ProgramNum , DA_Ai ,861 ,Ai ,861 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 68 | 68 | Clik1Action | Byte |  |  |  | 862 | Prgm 12 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 862 | 0x3D_Prgm 12Clik1Action , DA_Ai ,862 ,Ai ,862 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 69 | 69 | Clik2Action | Byte |  |  |  | 863 | Prgm 12 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 863 | 0x3D_Prgm 12Clik2Action , DA_Ai ,863 ,Ai ,863 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 70 | 70 | Clik3Action | Byte |  |  |  | 864 | Prgm 12 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 864 | 0x3D_Prgm 12Clik3Action , DA_Ai ,864 ,Ai ,864 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 71 | 71 | SSRainAction | Byte |  |  |  | 865 | Prgm 12 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 865 | 0x3D_Prgm 12SSRainAction , DA_Ai ,865 ,Ai ,865 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 72 | 72 | SSFreezeAction | Byte |  |  |  | 866 | Prgm 12 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 866 | 0x3D_Prgm 12SSFreezeAction , DA_Ai ,866 ,Ai ,866 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 73 | 73 | ProgramNum | Byte |  |  |  | 867 | Prgm 13 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 867 | 0x3D_Prgm 13ProgramNum , DA_Ai ,867 ,Ai ,867 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 74 | 74 | Clik1Action | Byte |  |  |  | 868 | Prgm 13 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 868 | 0x3D_Prgm 13Clik1Action , DA_Ai ,868 ,Ai ,868 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 75 | 75 | Clik2Action | Byte |  |  |  | 869 | Prgm 13 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 869 | 0x3D_Prgm 13Clik2Action , DA_Ai ,869 ,Ai ,869 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 76 | 76 | Clik3Action | Byte |  |  |  | 870 | Prgm 13 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 870 | 0x3D_Prgm 13Clik3Action , DA_Ai ,870 ,Ai ,870 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 77 | 77 | SSRainAction | Byte |  |  |  | 871 | Prgm 13 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 871 | 0x3D_Prgm 13SSRainAction , DA_Ai ,871 ,Ai ,871 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 78 | 78 | SSFreezeAction | Byte |  |  |  | 872 | Prgm 13 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 872 | 0x3D_Prgm 13SSFreezeAction , DA_Ai ,872 ,Ai ,872 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 79 | 79 | ProgramNum | Byte |  |  |  | 873 | Prgm 14 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 873 | 0x3D_Prgm 14ProgramNum , DA_Ai ,873 ,Ai ,873 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 80 | 80 | Clik1Action | Byte |  |  |  | 874 | Prgm 14 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 874 | 0x3D_Prgm 14Clik1Action , DA_Ai ,874 ,Ai ,874 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 81 | 81 | Clik2Action | Byte |  |  |  | 875 | Prgm 14 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 875 | 0x3D_Prgm 14Clik2Action , DA_Ai ,875 ,Ai ,875 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 82 | 82 | Clik3Action | Byte |  |  |  | 876 | Prgm 14 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 876 | 0x3D_Prgm 14Clik3Action , DA_Ai ,876 ,Ai ,876 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 83 | 83 | SSRainAction | Byte |  |  |  | 877 | Prgm 14 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 877 | 0x3D_Prgm 14SSRainAction , DA_Ai ,877 ,Ai ,877 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 84 | 84 | SSFreezeAction | Byte |  |  |  | 878 | Prgm 14 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 878 | 0x3D_Prgm 14SSFreezeAction , DA_Ai ,878 ,Ai ,878 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 85 | 85 | ProgramNum | Byte |  |  |  | 879 | Prgm 15 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 879 | 0x3D_Prgm 15ProgramNum , DA_Ai ,879 ,Ai ,879 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 86 | 86 | Clik1Action | Byte |  |  |  | 880 | Prgm 15 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 880 | 0x3D_Prgm 15Clik1Action , DA_Ai ,880 ,Ai ,880 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 87 | 87 | Clik2Action | Byte |  |  |  | 881 | Prgm 15 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 881 | 0x3D_Prgm 15Clik2Action , DA_Ai ,881 ,Ai ,881 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 88 | 88 | Clik3Action | Byte |  |  |  | 882 | Prgm 15 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 882 | 0x3D_Prgm 15Clik3Action , DA_Ai ,882 ,Ai ,882 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 89 | 89 | SSRainAction | Byte |  |  |  | 883 | Prgm 15 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 883 | 0x3D_Prgm 15SSRainAction , DA_Ai ,883 ,Ai ,883 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 90 | 90 | SSFreezeAction | Byte |  |  |  | 884 | Prgm 15 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 884 | 0x3D_Prgm 15SSFreezeAction , DA_Ai ,884 ,Ai ,884 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 91 | 91 | ProgramNum | Byte |  |  |  | 885 | Prgm 16 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 885 | 0x3D_Prgm 16ProgramNum , DA_Ai ,885 ,Ai ,885 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 92 | 92 | Clik1Action | Byte |  |  |  | 886 | Prgm 16 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 886 | 0x3D_Prgm 16Clik1Action , DA_Ai ,886 ,Ai ,886 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 93 | 93 | Clik2Action | Byte |  |  |  | 887 | Prgm 16 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 887 | 0x3D_Prgm 16Clik2Action , DA_Ai ,887 ,Ai ,887 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 94 | 94 | Clik3Action | Byte |  |  |  | 888 | Prgm 16 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 888 | 0x3D_Prgm 16Clik3Action , DA_Ai ,888 ,Ai ,888 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 95 | 95 | SSRainAction | Byte |  |  |  | 889 | Prgm 16 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 889 | 0x3D_Prgm 16SSRainAction , DA_Ai ,889 ,Ai ,889 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 96 | 96 | SSFreezeAction | Byte |  |  |  | 890 | Prgm 16 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 890 | 0x3D_Prgm 16SSFreezeAction , DA_Ai ,890 ,Ai ,890 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 97 | 97 | ProgramNum | Byte |  |  |  | 891 | Prgm 17 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 891 | 0x3D_Prgm 17ProgramNum , DA_Ai ,891 ,Ai ,891 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 98 | 98 | Clik1Action | Byte |  |  |  | 892 | Prgm 17 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 892 | 0x3D_Prgm 17Clik1Action , DA_Ai ,892 ,Ai ,892 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 99 | 99 | Clik2Action | Byte |  |  |  | 893 | Prgm 17 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 893 | 0x3D_Prgm 17Clik2Action , DA_Ai ,893 ,Ai ,893 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 100 | 100 | Clik3Action | Byte |  |  |  | 894 | Prgm 17 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 894 | 0x3D_Prgm 17Clik3Action , DA_Ai ,894 ,Ai ,894 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 101 | 101 | SSRainAction | Byte |  |  |  | 895 | Prgm 17 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 895 | 0x3D_Prgm 17SSRainAction , DA_Ai ,895 ,Ai ,895 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 102 | 102 | SSFreezeAction | Byte |  |  |  | 896 | Prgm 17 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 896 | 0x3D_Prgm 17SSFreezeAction , DA_Ai ,896 ,Ai ,896 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 103 | 103 | ProgramNum | Byte |  |  |  | 897 | Prgm 18 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 897 | 0x3D_Prgm 18ProgramNum , DA_Ai ,897 ,Ai ,897 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 104 | 104 | Clik1Action | Byte |  |  |  | 898 | Prgm 18 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 898 | 0x3D_Prgm 18Clik1Action , DA_Ai ,898 ,Ai ,898 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 105 | 105 | Clik2Action | Byte |  |  |  | 899 | Prgm 18 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 899 | 0x3D_Prgm 18Clik2Action , DA_Ai ,899 ,Ai ,899 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 106 | 106 | Clik3Action | Byte |  |  |  | 900 | Prgm 18 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 900 | 0x3D_Prgm 18Clik3Action , DA_Ai ,900 ,Ai ,900 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 107 | 107 | SSRainAction | Byte |  |  |  | 901 | Prgm 18 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 901 | 0x3D_Prgm 18SSRainAction , DA_Ai ,901 ,Ai ,901 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 108 | 108 | SSFreezeAction | Byte |  |  |  | 902 | Prgm 18 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 902 | 0x3D_Prgm 18SSFreezeAction , DA_Ai ,902 ,Ai ,902 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 109 | 109 | ProgramNum | Byte |  |  |  | 903 | Prgm 19 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 903 | 0x3D_Prgm 19ProgramNum , DA_Ai ,903 ,Ai ,903 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 110 | 110 | Clik1Action | Byte |  |  |  | 904 | Prgm 19 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 904 | 0x3D_Prgm 19Clik1Action , DA_Ai ,904 ,Ai ,904 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 111 | 111 | Clik2Action | Byte |  |  |  | 905 | Prgm 19 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 905 | 0x3D_Prgm 19Clik2Action , DA_Ai ,905 ,Ai ,905 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 112 | 112 | Clik3Action | Byte |  |  |  | 906 | Prgm 19 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 906 | 0x3D_Prgm 19Clik3Action , DA_Ai ,906 ,Ai ,906 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 113 | 113 | SSRainAction | Byte |  |  |  | 907 | Prgm 19 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 907 | 0x3D_Prgm 19SSRainAction , DA_Ai ,907 ,Ai ,907 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 114 | 114 | SSFreezeAction | Byte |  |  |  | 908 | Prgm 19 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 908 | 0x3D_Prgm 19SSFreezeAction , DA_Ai ,908 ,Ai ,908 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 115 | 115 | ProgramNum | Byte |  |  |  | 909 | Prgm 20 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 909 | 0x3D_Prgm 20ProgramNum , DA_Ai ,909 ,Ai ,909 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 116 | 116 | Clik1Action | Byte |  |  |  | 910 | Prgm 20 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 910 | 0x3D_Prgm 20Clik1Action , DA_Ai ,910 ,Ai ,910 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 117 | 117 | Clik2Action | Byte |  |  |  | 911 | Prgm 20 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 911 | 0x3D_Prgm 20Clik2Action , DA_Ai ,911 ,Ai ,911 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 118 | 118 | Clik3Action | Byte |  |  |  | 912 | Prgm 20 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 912 | 0x3D_Prgm 20Clik3Action , DA_Ai ,912 ,Ai ,912 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 119 | 119 | SSRainAction | Byte |  |  |  | 913 | Prgm 20 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 913 | 0x3D_Prgm 20SSRainAction , DA_Ai ,913 ,Ai ,913 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 120 | 120 | SSFreezeAction | Byte |  |  |  | 914 | Prgm 20 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 914 | 0x3D_Prgm 20SSFreezeAction , DA_Ai ,914 ,Ai ,914 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 121 | 121 | ProgramNum | Byte |  |  |  | 915 | Prgm 21 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 915 | 0x3D_Prgm 21ProgramNum , DA_Ai ,915 ,Ai ,915 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 122 | 122 | Clik1Action | Byte |  |  |  | 916 | Prgm 21 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 916 | 0x3D_Prgm 21Clik1Action , DA_Ai ,916 ,Ai ,916 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 123 | 123 | Clik2Action | Byte |  |  |  | 917 | Prgm 21 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 917 | 0x3D_Prgm 21Clik2Action , DA_Ai ,917 ,Ai ,917 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 124 | 124 | Clik3Action | Byte |  |  |  | 918 | Prgm 21 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 918 | 0x3D_Prgm 21Clik3Action , DA_Ai ,918 ,Ai ,918 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 125 | 125 | SSRainAction | Byte |  |  |  | 919 | Prgm 21 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 919 | 0x3D_Prgm 21SSRainAction , DA_Ai ,919 ,Ai ,919 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 126 | 126 | SSFreezeAction | Byte |  |  |  | 920 | Prgm 21 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 920 | 0x3D_Prgm 21SSFreezeAction , DA_Ai ,920 ,Ai ,920 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 127 | 127 | ProgramNum | Byte |  |  |  | 921 | Prgm 22 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 921 | 0x3D_Prgm 22ProgramNum , DA_Ai ,921 ,Ai ,921 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 128 | 128 | Clik1Action | Byte |  |  |  | 922 | Prgm 22 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 922 | 0x3D_Prgm 22Clik1Action , DA_Ai ,922 ,Ai ,922 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 129 | 129 | Clik2Action | Byte |  |  |  | 923 | Prgm 22 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 923 | 0x3D_Prgm 22Clik2Action , DA_Ai ,923 ,Ai ,923 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 130 | 130 | Clik3Action | Byte |  |  |  | 924 | Prgm 22 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 924 | 0x3D_Prgm 22Clik3Action , DA_Ai ,924 ,Ai ,924 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 131 | 131 | SSRainAction | Byte |  |  |  | 925 | Prgm 22 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 925 | 0x3D_Prgm 22SSRainAction , DA_Ai ,925 ,Ai ,925 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 132 | 132 | SSFreezeAction | Byte |  |  |  | 926 | Prgm 22 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 926 | 0x3D_Prgm 22SSFreezeAction , DA_Ai ,926 ,Ai ,926 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 133 | 133 | ProgramNum | Byte |  |  |  | 927 | Prgm 23 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 927 | 0x3D_Prgm 23ProgramNum , DA_Ai ,927 ,Ai ,927 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 134 | 134 | Clik1Action | Byte |  |  |  | 928 | Prgm 23 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 928 | 0x3D_Prgm 23Clik1Action , DA_Ai ,928 ,Ai ,928 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 135 | 135 | Clik2Action | Byte |  |  |  | 929 | Prgm 23 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 929 | 0x3D_Prgm 23Clik2Action , DA_Ai ,929 ,Ai ,929 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 136 | 136 | Clik3Action | Byte |  |  |  | 930 | Prgm 23 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 930 | 0x3D_Prgm 23Clik3Action , DA_Ai ,930 ,Ai ,930 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 137 | 137 | SSRainAction | Byte |  |  |  | 931 | Prgm 23 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 931 | 0x3D_Prgm 23SSRainAction , DA_Ai ,931 ,Ai ,931 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 138 | 138 | SSFreezeAction | Byte |  |  |  | 932 | Prgm 23 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 932 | 0x3D_Prgm 23SSFreezeAction , DA_Ai ,932 ,Ai ,932 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 139 | 139 | ProgramNum | Byte |  |  |  | 933 | Prgm 24 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 933 | 0x3D_Prgm 24ProgramNum , DA_Ai ,933 ,Ai ,933 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 140 | 140 | Clik1Action | Byte |  |  |  | 934 | Prgm 24 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 934 | 0x3D_Prgm 24Clik1Action , DA_Ai ,934 ,Ai ,934 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 141 | 141 | Clik2Action | Byte |  |  |  | 935 | Prgm 24 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 935 | 0x3D_Prgm 24Clik2Action , DA_Ai ,935 ,Ai ,935 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 142 | 142 | Clik3Action | Byte |  |  |  | 936 | Prgm 24 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 936 | 0x3D_Prgm 24Clik3Action , DA_Ai ,936 ,Ai ,936 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 143 | 143 | SSRainAction | Byte |  |  |  | 937 | Prgm 24 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 937 | 0x3D_Prgm 24SSRainAction , DA_Ai ,937 ,Ai ,937 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 144 | 144 | SSFreezeAction | Byte |  |  |  | 938 | Prgm 24 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 938 | 0x3D_Prgm 24SSFreezeAction , DA_Ai ,938 ,Ai ,938 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 145 | 145 | ProgramNum | Byte |  |  |  | 939 | Prgm 25 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 939 | 0x3D_Prgm 25ProgramNum , DA_Ai ,939 ,Ai ,939 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 146 | 146 | Clik1Action | Byte |  |  |  | 940 | Prgm 25 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 940 | 0x3D_Prgm 25Clik1Action , DA_Ai ,940 ,Ai ,940 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 147 | 147 | Clik2Action | Byte |  |  |  | 941 | Prgm 25 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 941 | 0x3D_Prgm 25Clik2Action , DA_Ai ,941 ,Ai ,941 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 148 | 148 | Clik3Action | Byte |  |  |  | 942 | Prgm 25 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 942 | 0x3D_Prgm 25Clik3Action , DA_Ai ,942 ,Ai ,942 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 149 | 149 | SSRainAction | Byte |  |  |  | 943 | Prgm 25 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 943 | 0x3D_Prgm 25SSRainAction , DA_Ai ,943 ,Ai ,943 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 150 | 150 | SSFreezeAction | Byte |  |  |  | 944 | Prgm 25 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 944 | 0x3D_Prgm 25SSFreezeAction , DA_Ai ,944 ,Ai ,944 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 151 | 151 | ProgramNum | Byte |  |  |  | 945 | Prgm 26 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 945 | 0x3D_Prgm 26ProgramNum , DA_Ai ,945 ,Ai ,945 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 152 | 152 | Clik1Action | Byte |  |  |  | 946 | Prgm 26 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 946 | 0x3D_Prgm 26Clik1Action , DA_Ai ,946 ,Ai ,946 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 153 | 153 | Clik2Action | Byte |  |  |  | 947 | Prgm 26 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 947 | 0x3D_Prgm 26Clik2Action , DA_Ai ,947 ,Ai ,947 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 154 | 154 | Clik3Action | Byte |  |  |  | 948 | Prgm 26 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 948 | 0x3D_Prgm 26Clik3Action , DA_Ai ,948 ,Ai ,948 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 155 | 155 | SSRainAction | Byte |  |  |  | 949 | Prgm 26 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 949 | 0x3D_Prgm 26SSRainAction , DA_Ai ,949 ,Ai ,949 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 156 | 156 | SSFreezeAction | Byte |  |  |  | 950 | Prgm 26 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 950 | 0x3D_Prgm 26SSFreezeAction , DA_Ai ,950 ,Ai ,950 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 157 | 157 | ProgramNum | Byte |  |  |  | 951 | Prgm 27 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 951 | 0x3D_Prgm 27ProgramNum , DA_Ai ,951 ,Ai ,951 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 158 | 158 | Clik1Action | Byte |  |  |  | 952 | Prgm 27 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 952 | 0x3D_Prgm 27Clik1Action , DA_Ai ,952 ,Ai ,952 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 159 | 159 | Clik2Action | Byte |  |  |  | 953 | Prgm 27 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 953 | 0x3D_Prgm 27Clik2Action , DA_Ai ,953 ,Ai ,953 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 160 | 160 | Clik3Action | Byte |  |  |  | 954 | Prgm 27 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 954 | 0x3D_Prgm 27Clik3Action , DA_Ai ,954 ,Ai ,954 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 161 | 161 | SSRainAction | Byte |  |  |  | 955 | Prgm 27 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 955 | 0x3D_Prgm 27SSRainAction , DA_Ai ,955 ,Ai ,955 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 162 | 162 | SSFreezeAction | Byte |  |  |  | 956 | Prgm 27 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 956 | 0x3D_Prgm 27SSFreezeAction , DA_Ai ,956 ,Ai ,956 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 163 | 163 | ProgramNum | Byte |  |  |  | 957 | Prgm 28 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 957 | 0x3D_Prgm 28ProgramNum , DA_Ai ,957 ,Ai ,957 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 164 | 164 | Clik1Action | Byte |  |  |  | 958 | Prgm 28 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 958 | 0x3D_Prgm 28Clik1Action , DA_Ai ,958 ,Ai ,958 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 165 | 165 | Clik2Action | Byte |  |  |  | 959 | Prgm 28 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 959 | 0x3D_Prgm 28Clik2Action , DA_Ai ,959 ,Ai ,959 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 166 | 166 | Clik3Action | Byte |  |  |  | 960 | Prgm 28 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 960 | 0x3D_Prgm 28Clik3Action , DA_Ai ,960 ,Ai ,960 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 167 | 167 | SSRainAction | Byte |  |  |  | 961 | Prgm 28 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 961 | 0x3D_Prgm 28SSRainAction , DA_Ai ,961 ,Ai ,961 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 168 | 168 | SSFreezeAction | Byte |  |  |  | 962 | Prgm 28 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 962 | 0x3D_Prgm 28SSFreezeAction , DA_Ai ,962 ,Ai ,962 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 169 | 169 | ProgramNum | Byte |  |  |  | 963 | Prgm 29 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 963 | 0x3D_Prgm 29ProgramNum , DA_Ai ,963 ,Ai ,963 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 170 | 170 | Clik1Action | Byte |  |  |  | 964 | Prgm 29 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 964 | 0x3D_Prgm 29Clik1Action , DA_Ai ,964 ,Ai ,964 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 171 | 171 | Clik2Action | Byte |  |  |  | 965 | Prgm 29 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 965 | 0x3D_Prgm 29Clik2Action , DA_Ai ,965 ,Ai ,965 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 172 | 172 | Clik3Action | Byte |  |  |  | 966 | Prgm 29 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 966 | 0x3D_Prgm 29Clik3Action , DA_Ai ,966 ,Ai ,966 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 173 | 173 | SSRainAction | Byte |  |  |  | 967 | Prgm 29 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 967 | 0x3D_Prgm 29SSRainAction , DA_Ai ,967 ,Ai ,967 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 174 | 174 | SSFreezeAction | Byte |  |  |  | 968 | Prgm 29 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 968 | 0x3D_Prgm 29SSFreezeAction , DA_Ai ,968 ,Ai ,968 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 175 | 175 | ProgramNum | Byte |  |  |  | 969 | Prgm 30 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 969 | 0x3D_Prgm 30ProgramNum , DA_Ai ,969 ,Ai ,969 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 176 | 176 | Clik1Action | Byte |  |  |  | 970 | Prgm 30 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 970 | 0x3D_Prgm 30Clik1Action , DA_Ai ,970 ,Ai ,970 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 177 | 177 | Clik2Action | Byte |  |  |  | 971 | Prgm 30 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 971 | 0x3D_Prgm 30Clik2Action , DA_Ai ,971 ,Ai ,971 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 178 | 178 | Clik3Action | Byte |  |  |  | 972 | Prgm 30 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 972 | 0x3D_Prgm 30Clik3Action , DA_Ai ,972 ,Ai ,972 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 179 | 179 | SSRainAction | Byte |  |  |  | 973 | Prgm 30 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 973 | 0x3D_Prgm 30SSRainAction , DA_Ai ,973 ,Ai ,973 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 180 | 180 | SSFreezeAction | Byte |  |  |  | 974 | Prgm 30 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 974 | 0x3D_Prgm 30SSFreezeAction , DA_Ai ,974 ,Ai ,974 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 181 | 181 | ProgramNum | Byte |  |  |  | 975 | Prgm 31 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 975 | 0x3D_Prgm 31ProgramNum , DA_Ai ,975 ,Ai ,975 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 182 | 182 | Clik1Action | Byte |  |  |  | 976 | Prgm 31 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 976 | 0x3D_Prgm 31Clik1Action , DA_Ai ,976 ,Ai ,976 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 183 | 183 | Clik2Action | Byte |  |  |  | 977 | Prgm 31 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 977 | 0x3D_Prgm 31Clik2Action , DA_Ai ,977 ,Ai ,977 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 184 | 184 | Clik3Action | Byte |  |  |  | 978 | Prgm 31 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 978 | 0x3D_Prgm 31Clik3Action , DA_Ai ,978 ,Ai ,978 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 185 | 185 | SSRainAction | Byte |  |  |  | 979 | Prgm 31 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 979 | 0x3D_Prgm 31SSRainAction , DA_Ai ,979 ,Ai ,979 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 186 | 186 | SSFreezeAction | Byte |  |  |  | 980 | Prgm 31 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 980 | 0x3D_Prgm 31SSFreezeAction , DA_Ai ,980 ,Ai ,980 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
0x3D | 187 | 187 | ProgramNum | Byte |  |  |  | 981 | Prgm 32 | Program Number for which the Sensor is being sent. Range is 1 to 32. | 000 | Ai | 981 | 0x3D_Prgm 32ProgramNum , DA_Ai ,981 ,Ai ,981 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Program Number for which the Sensor is ,
0x3D | 188 | 188 | Clik1Action | Byte |  |  |  | 982 | Prgm 32 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 982 | 0x3D_Prgm 32Clik1Action , DA_Ai ,982 ,Ai ,982 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 189 | 189 | Clik2Action | Byte |  |  |  | 983 | Prgm 32 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 983 | 0x3D_Prgm 32Clik2Action , DA_Ai ,983 ,Ai ,983 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 190 | 190 | Clik3Action | Byte |  |  |  | 984 | Prgm 32 | Action to take when the specified Clik sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 984 | 0x3D_Prgm 32Clik3Action , DA_Ai ,984 ,Ai ,984 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the specified Clik ,
0x3D | 191 | 191 | SSRainAction | Byte |  |  |  | 985 | Prgm 32 | Action to take when the Solar Sync Rain sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 985 | 0x3D_Prgm 32SSRainAction , DA_Ai ,985 ,Ai ,985 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Rain ,
0x3D | 192 | 192 | SSFreezeAction | Byte |  |  |  | 986 | Prgm 32 | Action to take when the Solar Sync Freeze sensor is active. Range is 0 to 2. 0 = Ignore- 1 = Suspend- 2 = Pause. | 000 | Ai | 986 | 0x3D_Prgm 32SSFreezeAction , DA_Ai ,986 ,Ai ,986 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Action to take when the Solar Sync Free ,
000
0x3E – REPORT FIELD CONTROLLER PROGRAM HEADER DATA (v2.13.000 and Later) | [10 empty] | 000 |  |  |  |  | 0x3E – REPORT FIELD CONTROLLER PROGRAM HEADER DATA (v2.13.000 and Later)
| demo=h1e.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
000
| Transmits from a field controller, header data of a speific Field Controller Program. A FCP header is information global to the specified program. It includes various items of a program including the program #, mode, start time(s), schedule, seasonal adjust, no water window times, and event delays. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x3E | 0 |  | Trigger Read |  |  | 37 |  |  |  | Not used | 000 | Av | 37 | 0x3E_Trigger Read , DA_Av ,037 ,Av ,037 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Not used ,
0x3E | 1 | 1 | Program# | Byte |  |  |  | 987 |  | Value indicates the Program Number for which the header data is being sent. Range is 1 to 32. | 000 | Ai | 987 | 0x3E_Program# , DA_Ai ,987 ,Ai ,987 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Program Number for ,
0x3E | 2 | 2 | StackMode | Byte |  |  |  | 988 |  | Value indicates the Stacking Mode for the Program. Range is 0 to 1. 0 = Stack Mode- 1 = Overlap Mode. | 000 | Ai | 988 | 0x3E_StackMode , DA_Ai ,988 ,Ai ,988 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Stacking Mode for t ,
0x3E | 3 | 3 | ScheduleType | Byte |  |  |  | 989 |  | Value indicates the Porgram Type for the Program. Range is 0 to 3. 0 = Day of Week- 1 = Odd/Even- 2 = Interval- 3 = Manual Only | 000 | Ai | 989 | 0x3E_ScheduleType , DA_Ai ,989 ,Ai ,989 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicates the Porgram Type for th ,
0x3E | 4 | 4 | DOWDays | Uint16 |  |  |  | 990 |  | Bitmap indicating the Day of Week Schedule. Indicates days to water (0 = No Water- 1 = Water). Default is all days on. Bits 15-7: Not Used. Bits 6-0: Sunday- Saturday … Monday. | 000 | Ai | 990 | 0x3E_DOWDays , DA_Ai ,990 ,Ai ,990 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap indicating the Day of Week Sched ,
0x3E | 5 | 5 | OddEvenDays | Uint16 |  |  |  | 991 |  | Bitmap indicating the Odd/Even Schedule and No Water Days ( 0 = Water- 1 = No Water). Default is Odd Days- and all No Waters Days all set to zero. | 000 | Ai | 991 | 0x3E_OddEvenDays , DA_Ai ,991 ,Ai ,991 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap indicating the Odd/Even Schedule ,
0x3E | 6 | 6 | IntervalDays | Uint16 |  |  |  | 992 |  | Bitmap indicating the No Water Days (0 = Water- 1 = No Water). Default is all No Water Days set to zero. Bits 15 - 7: Not used. Bits 6-0: Sunday- Saturday … Monday. | 000 | Ai | 992 | 0x3E_IntervalDays , DA_Ai ,992 ,Ai ,992 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Bitmap indicating the No Water Days (0 ,
0x3E | 7 | 7 | IntLength | Byte |  |  |  | 993 |  | Byte value indicating the length of the interval schedule. Range is 2 to 31. Default is 2. | 000 | Ai | 993 | 0x3E_IntLength , DA_Ai ,993 ,Ai ,993 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Byte value indicating the length of the ,
0x3E | 8 | 8 | IntNextWater | Byte |  |  |  | 994 |  | Value indicating the number of days before next water day. Range is 0 to 30. Must be at least one less than interval length. Default is 0. | 000 | Ai | 994 | 0x3E_IntNextWater , DA_Ai ,994 ,Ai ,994 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of days bef ,
0x3E | 9 | 9 | StartType | Byte |  |  |  | 995 |  | Value indicating the Start Time Type. Range is 0 to 2. 0=Auto- 1 = Start to End- 2 = Manual. | 000 | Ai | 995 | 0x3E_StartType , DA_Ai ,995 ,Ai ,995 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Start Time Type. R ,
0x3E | 10 | 10 | StartTime1 | UINT16 |  |  |  | 996 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 996 | 0x3E_StartTime1 , DA_Ai ,996 ,Ai ,996 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 11 | 11 | StartTime2 | UINT16 |  |  |  | 997 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 997 | 0x3E_StartTime2 , DA_Ai ,997 ,Ai ,997 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 12 | 12 | StartTime3 | UINT16 |  |  |  | 998 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 998 | 0x3E_StartTime3 , DA_Ai ,998 ,Ai ,998 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 13 | 13 | StartTime4 | UINT16 |  |  |  | 999 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 999 | 0x3E_StartTime4 , DA_Ai ,999 ,Ai ,999 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 14 | 14 | StartTime5 | UINT16 |  |  |  | 1000 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 1000 | 0x3E_StartTime5 , DA_Ai ,1000 ,Ai ,1000 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 15 | 15 | StartTime6 | UINT16 |  |  |  | 1001 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 1001 | 0x3E_StartTime6 , DA_Ai ,1001 ,Ai ,1001 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 16 | 16 | StartTime7 | UINT16 |  |  |  | 1002 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 1002 | 0x3E_StartTime7 , DA_Ai ,1002 ,Ai ,1002 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 17 | 17 | StartTime8 | UINT16 |  |  |  | 1003 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 1003 | 0x3E_StartTime8 , DA_Ai ,1003 ,Ai ,1003 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 18 | 18 | StartTime9 | UINT16 |  |  |  | 1004 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 1004 | 0x3E_StartTime9 , DA_Ai ,1004 ,Ai ,1004 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 19 | 19 | StartTime10 | UINT16 |  |  |  | 1005 |  | Values indicating the ten Auto Start Times for the program in Minutes after idnight. Range is 0-1439. OFF is indicated by FFFFH. | 000 | Ai | 1005 | 0x3E_StartTime10 , DA_Ai ,1005 ,Ai ,1005 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Values indicating the ten Auto Start Ti ,
0x3E | 20 | 20 | SeasAdjSource | Byte |  |  |  | 1006 |  | Value indicating the Seasonal Adjust Source to use for the Program. Range in 0 to 3. 0 = Program Seasonal Adjust. 1 = Global Seasonal Adjust. 2 = Global Monthly Seasonal Adjust. 3 = Solar Sync Seasonal Adjust. | 000 | Ai | 1006 | 0x3E_SeasAdjSource , DA_Ai ,1006 ,Ai ,1006 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Seasonal Adjust So ,
0x3E | 21 | 21 | SeasonalAdjust | Uint16 |  |  |  | 1007 |  | Value indicating the Program Seasonal Adjust value. Range is 0 to 300. | 000 | Ai | 1007 | 0x3E_SeasonalAdjust , DA_Ai ,1007 ,Ai ,1007 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Program Seasonal A ,
0x3E | 22 | 22 | IgnoreCalDaysOff | Byte |  |  |  | 1008 |  | Value indicating whether to ignore any Calendar Days Off for this Program. Range is 0 to 1. 0 = Do not ignore. 1 = Ignore. | 000 | Ai | 1008 | 0x3E_IgnoreCalDaysOff , DA_Ai ,1008 ,Ai ,1008 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether to ignore any ,
0x3E | 23 | 23 | NWWStart | Uint16 |  |  |  | 1009 |  | Start time for program No Water Window in Minutes After Midnight. Range is 0 to 1439. Not Used in indicated by FFFFH. | 000 | Ai | 1009 | 0x3E_NWWStart , DA_Ai ,1009 ,Ai ,1009 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Start time for program No Water Window ,
0x3E | 24 | 24 | NWWEnd | Uint16 |  |  |  | 1010 |  | End time for program No Water Window in Minutes After Midnight. Range in 0-1439. Not Used is indicated by FFFFH. If not set to Not Used- must be greater or equal to the NWWStart value. | 000 | Ai | 1010 | 0x3E_NWWEnd , DA_Ai ,1010 ,Ai ,1010 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,End time for program No Water Window in ,
0x3E | 25 | 25 | EventDelay | Uint16 |  |  |  | 1011 |  | Value indicating the amount of time in seconds to delay between Events. Range is 0 to 21-600 (6 Hours). | 000 | Ai | 1011 | 0x3E_EventDelay , DA_Ai ,1011 ,Ai ,1011 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the amount of time in ,
0x3E | 26 | 26 | STEStartTime | Uint16 |  |  |  | 1012 |  | Value indicating the Start to End Start Type Start Time for the program in Minutes After Midnight. Range is 0 - 1439. OFF is indicated by FFFFH. | 000 | Ai | 1012 | 0x3E_STEStartTime , DA_Ai ,1012 ,Ai ,1012 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Start to End Start ,
0x3E | 27 | 27 | STTEEndTime | Uint16 |  |  |  | 1013 |  | Value indicating the Start to End Start Type Start Time for the program in Minutes After Midnight. Range is 0 - 1439. OFF is indicated by FFFFH. | 000 | Ai | 1013 | 0x3E_STTEEndTime , DA_Ai ,1013 ,Ai ,1013 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Start to End Start ,
000
0x3F – Report Field Controller Program Event Run Time Data | [10 empty] | 000 |  |  |  |  | 0x3F – Report Field Controller Program Event Run Time Data
| Reports Event Run Time data for a FCP program, consisting of a Program number, followed by a sequence of Event Types (Stations and/or Blocks) and Run Times starting at the specified Event Number. Only events with run times are transmitted and multiple requests of this command may be required to retrieve all the events since only 48 of the Program’s 64 events fit in a single transmission. The starting Event Number is sent in the request for this purpose. If a request is made to return events and full message of 48 events are returned, then a 2nd request will be necessary to get any remaining events | [9 empty] | 000
| Not Implemented | [9 empty] | 000
000
0x40 - Set User Management Information | [10 empty] | 000 |  |  |  |  | 0x40 - Set User Management Information
0x41 - Report User Management Information | [10 empty] | 000 |  |  |  |  | 0x41 - Report User Management Information
| Not Implemented | [9 empty] | 000
000
0x42 – Set Calendar Days Off |  | Not working | [8 empty] | 000 |  |  |  |  | 0x42 – Set Calendar Days Off
| demo=h42.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
| This command sends a list of calendar dates to be used as Calendar Days Off in the controller. On these dates, program watering will be disabled unless a program is set to ignore Calendar Days Off. Dates may be specified up to 1 year in advance of the current date. | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x42 | 0 | 1 | Trigger |  | 23 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 23 | 0x42_Trigger , DA_Bv ,023 ,Bv ,023 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x42 | 1 | 2 | Date 01 | Uint16 |  | 357 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 357 | 0x42_Date 01 , DA_Av ,357 ,Av ,357 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 2 | 3 | Date 02 | Uint16 |  | 358 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 358 | 0x42_Date 02 , DA_Av ,358 ,Av ,358 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 3 | 4 | Date 03 | Uint16 |  | 359 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 359 | 0x42_Date 03 , DA_Av ,359 ,Av ,359 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 4 | 5 | Date 04 | Uint16 |  | 360 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 360 | 0x42_Date 04 , DA_Av ,360 ,Av ,360 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 5 | 6 | Date 05 | Uint16 |  | 361 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 361 | 0x42_Date 05 , DA_Av ,361 ,Av ,361 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 6 | 7 | Date 06 | Uint16 |  | 362 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 362 | 0x42_Date 06 , DA_Av ,362 ,Av ,362 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 7 | 8 | Date 07 | Uint16 |  | 363 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 363 | 0x42_Date 07 , DA_Av ,363 ,Av ,363 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 8 | 9 | Date 08 | Uint16 |  | 364 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 364 | 0x42_Date 08 , DA_Av ,364 ,Av ,364 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 9 | 10 | Date 09 | Uint16 |  | 365 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 365 | 0x42_Date 09 , DA_Av ,365 ,Av ,365 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 10 | 11 | Date 10 | Uint16 |  | 366 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 366 | 0x42_Date 10 , DA_Av ,366 ,Av ,366 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 11 | 12 | Date 11 | Uint16 |  | 367 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 367 | 0x42_Date 11 , DA_Av ,367 ,Av ,367 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x42 | 12 | 13 | Date 12 | Uint16 |  | 368 |  |  |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Av | 368 | 0x42_Date 12 , DA_Av ,368 ,Av ,368 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
000
000
000
0x43 – Get Calendar Days Off |  | Not working | [8 empty] | 000 |  |  |  |  | 0x43 – Get Calendar Days Off
| demo=h42.html | [9 empty] | 000
| template=type1.html | [9 empty] | 000
| This command reports the list of calendar dates to be used as Calendar Days Off in the controller back to the central. On these dates, program watering will be disabled unless a program is set to ignore Calendar Days Off. Dates may be up to 1 year in advance of the current date. | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x43 | 0 | [8 empty] | Not used | 000
0x43 | 1 | 1 | Date 01 | Uint16 |  |  |  | 1014 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1014 | 0x43_Date 01 , DA_Ai ,1014 ,Ai ,1014 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 2 | 2 | Date 02 | Uint16 |  |  |  | 1015 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1015 | 0x43_Date 02 , DA_Ai ,1015 ,Ai ,1015 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 3 | 3 | Date 03 | Uint16 |  |  |  | 1016 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1016 | 0x43_Date 03 , DA_Ai ,1016 ,Ai ,1016 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 4 | 4 | Date 04 | Uint16 |  |  |  | 1017 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1017 | 0x43_Date 04 , DA_Ai ,1017 ,Ai ,1017 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 5 | 5 | Date 05 | Uint16 |  |  |  | 1018 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1018 | 0x43_Date 05 , DA_Ai ,1018 ,Ai ,1018 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 6 | 6 | Date 06 | Uint16 |  |  |  | 1019 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1019 | 0x43_Date 06 , DA_Ai ,1019 ,Ai ,1019 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 7 | 7 | Date 07 | Uint16 |  |  |  | 1020 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1020 | 0x43_Date 07 , DA_Ai ,1020 ,Ai ,1020 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 8 | 8 | Date 08 | Uint16 |  |  |  | 1021 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1021 | 0x43_Date 08 , DA_Ai ,1021 ,Ai ,1021 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 9 | 9 | Date 09 | Uint16 |  |  |  | 1022 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1022 | 0x43_Date 09 , DA_Ai ,1022 ,Ai ,1022 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 10 | 10 | Date 10 | Uint16 |  |  |  | 1023 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1023 | 0x43_Date 10 , DA_Ai ,1023 ,Ai ,1023 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 11 | 11 | Date 11 | Uint16 |  |  |  | 1024 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1024 | 0x43_Date 11 , DA_Ai ,1024 ,Ai ,1024 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
0x43 | 12 | 12 | Date 12 | Uint16 |  |  |  | 1025 |  | Value indicating a Unix Time to use as Calendar Days Off. Unix Time must be set to 12am of the desired date. Range is Unix Time of today at 12am to Unix Time at 12am one year from today. A special value of 0xFFFFFFFF is used to specify that the date is not used. | 000 | Ai | 1025 | 0x43_Date 12 , DA_Ai ,1025 ,Ai ,1025 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating a Unix Time to use as ,
000
0x44-0x4e | [10 empty] | 000
| Reserved for later use by Hunter | [9 empty] | 000
000
0x4f - Report Item CRCs | [10 empty] | 000 |  |  |  |  | 0x4f - Report Item CRCs
| Not Implemented | [9 empty] | 000
000
0x50 | [10 empty] | 000
| Reserved for later use by Hunter | [9 empty] | 000
000
0x51 – Stop Irrigation | [10 empty] | 000 |  |  |  |  | 0x51 – Stop Irrigation
| Transmits to field controller(s), a command to immediately stop all active events. Irrigation resumes at the next event start or other operation | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x51 – Stop Irrigation | 0 | 1 | Trigger_StopIrrigation |  | 24 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 24 | 0x51_Trigger_StopIrrigation , DA_Bv ,024 ,Bv ,024 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti , |  | 0x51 – Stop Irrigation
| demo=cmds.html | [9 empty] | 000
| N/A Command does not carry data | [9 empty] | 000
000
0x52 – Programmable Off | [10 empty] | 000 |  |  |  |  | 0x52 – Programmable Off
| Transmits to field controller(s), a command to immediately stop all active events. Irrigation resumes at the next event start or other operation. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x52 | 0 | 1 | Trigger_ProgramableOff |  | 25 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 25 | 0x52_Trigger_ProgramableOff , DA_Bv ,025 ,Bv ,025 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x52 | 1 | 2 | Days | Byte |  | 369 |  |  |  | Value contains the number of days to set for the shutdown. Range is 0-180. A value of 0 indicates an indefinite shutdown. | 000 | Av | 369 | 0x52_Days , DA_Av ,369 ,Av ,369 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains the number of days to se ,
000
0x53 – Suspend Irrigation | [10 empty] | 000 |  |  |  |  | 0x53 – Suspend Irrigation
| demo=cmds.html | [9 empty] | 000
| Transmits to field controller(s), a command to immediately stop all active events and cancels all programs currently running. Irrigation does not resume until mode is canceled by a Central or through the keypad at the controller, or the day counter reaches 0. | [9 empty] | 000
| Extracts the Number of Days from the Data array and then sends cmd. | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x53 | 0 | 1 | Trigger_SuspendIrrigation |  | 26 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 26 | 0x53_Trigger_SuspendIrrigation , DA_Bv ,026 ,Bv ,026 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
| N/A Command does not carry data | [9 empty] | 000
000
0x54 – Cancel Programmable Off | [10 empty] | 000 |  |  |  |  | 0x54 – Cancel Programmable Off
| demo=cmds.html | [9 empty] | 000
| Cancels Programmable Off and allows irrigation to resume. If Controller is not shutdown, no action is taken. This command is normally used with the ‘All Call’ address 1940, but controllers can be addressed individually. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x54 | 0 | 1 | Trigger_CancelPrgramableOff |  | 27 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 27 | 0x54_Trigger_CancelPrgramableOff , DA_Bv ,027 ,Bv ,027 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
| N/A Command does not carry data | [9 empty] | 000
000
0x55 – Cancel Suspend | [10 empty] | 000 |  |  |  |  | 0x55 – Cancel Suspend
| demo=cmds.html | [9 empty] | 000
| Cancels Suspend mode and allows irrigation to resume. If Controller is not in Suspend, no action is taken | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x55 | 0 | 1 | Trigger_CancelSuspend |  | 28 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 28 | 0x55_Trigger_CancelSuspend , DA_Bv ,028 ,Bv ,028 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
| N/A Command does not carry data | [9 empty] | 000
000
0x56 – Start Manual All Station Program | [10 empty] | 000 |  |  |  |  | 0x56 – Start Manual All Station Program
| demo=h56.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
| Starts the specified FCP from the specified starting point. All stations from the starting point forward will run as programmed. Command | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x56 | 0 | 1 | Trigger_StartManAllStnPrgm |  | 29 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 29 | 0x56_Trigger_StartManAllStnPrgm , DA_Bv ,029 ,Bv ,029 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x56 | 1 | 2 | Program# | Byte |  | 370 |  |  |  | Value containing the Program Number to start. Range is 1 to 32. | 000 | Av | 370 | 0x56_Program# , DA_Av ,370 ,Av ,370 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing the Program Number to ,
0x56 | 2 | 3 | StartPoint | Byte |  | 371 |  |  |  | Value indicating the point within the Program to start executing events. Range is 0 to 1. 0 = Start at beginning of Program. 1 = Start at specified Event Number. 2 = Start at first instance of specified Station Number. 3 = Start at first instance of specified Block Number. | 000 | Av | 371 | 0x56_StartPoint , DA_Av ,371 ,Av ,371 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the point within the P ,
0x56 | 3 | 4 | Number | Uint16 |  | 372 |  |  |  | Value containing the Event- Station- or Block Number from which to start the Program. Ranges are as follows: Program Beginning: Rang is N/A. Value is ignored. Event Number: Range is 1 to 64. Station Number: Range is 1 to 54 for Conventional Controllers - 1 to 225 for Decoder controllers. Block Number: Range is 1 to 64. | 000 | Av | 372 | 0x56_Number , DA_Av ,372 ,Av ,372 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing the Event- Station- or ,
000
0x57 – Set System Event Mode | [10 empty] | 000 |  |  |  |  | 0x57 – Set System Event Mode
0x58 – Set FCP Mode | [10 empty] | 000 |  |  |  |  | 0x58 – Set FCP Mode
| Reserved for later use by Hunter | [9 empty] | 000
000
0x59 – Clear Field Controller Display Messages | [10 empty] | 000 |  |  |  |  | 0x59 – Clear Field Controller Display Messages
| demo=cmds.html | [9 empty] | 000
| This command emulates the action of pressing the “Clear Messages” soft key on the Field Controller faceplate when viewing the Attention Messages with one exception. It will clear all Attention Messages from the list and clear the alarm icon. However, it will not clear the Alarm and Info bits as is done when the Attention Messages are cleared via the controller’s UI. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x59 | 0 | 1 | Trigger_ClearDisplay |  | 30 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 30 | 0x59_Trigger_ClearDisplay , DA_Bv ,030 ,Bv ,030 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
| N/A Command does not carry data | [9 empty] | 000
000
0x5A – Set Pause Mode | [10 empty] | 000 |  |  |  |  | 0x5A – Set Pause Mode
| demo=cmds.html | [9 empty] | 000
| This command places the controller in a pause mode for up to 30 minutes. Pause will stop irrigation and stop all run time clocks. This is the same command as pressing the Pause button on the controller faceplate. The command can be cancelled by a command from the Central, by pressing the Pause button again on the controller faceplate, or when the Pause timer reaches 0. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x5A | 0 | 1 | Trigger_SetPauseMode |  | 31 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 31 | 0x5A_Trigger_SetPauseMode , DA_Bv ,031 ,Bv ,031 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
| N/A Command does not carry data | [9 empty] | 000
000
0x5B – Cancel Pause Mode | [10 empty] | 000 |  |  |  |  | 0x5B – Cancel Pause Mode
| demo=cmds.html | [9 empty] | 000
000
| Cancel Pause mode to allow irrigation to resume. If Controller is not in Pause, no action is taken. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | [9 empty] | 000
0x5B | 0 | item | Variable/ Data | Data Type | [5 empty] | Description | 000
| N/A Command does not carry data | 1 | Trigger_CancelPause |  | 32 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 32 | _Trigger_CancelPause , DA_Bv ,032 ,Bv ,032 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
000
000
0x5C – Start Single Manual Event | [10 empty] | 000 |  |  |  |  | 0x5C – Start Single Manual Event
| demo=h5c.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
000
| Starts the specified single Station, Block, or P/MV for the specified time. | [9 empty] | 000
| This command and the response do not carry a payload of data | [9 empty] | 000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x5C | 0 | 1 | Trigger_StartManualEvent |  | 33 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 33 | 0x5C_Trigger_StartManualEvent , DA_Bv ,033 ,Bv ,033 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x5C | 1 | 2 | Device | Byte |  | 373 |  |  |  | Value indicting the type of device to start manually. Range is 1 to 3. 1 = Station. 2 = Block. 3 = P/MV. | 000 | Av | 373 | 0x5C_Device , DA_Av ,373 ,Av ,373 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicting the type of device to s ,
0x5C | 2 | 3 | Number | Uint16 |  | 374 |  |  |  | Value indicating the number of specified device. May be a Station- Block- or P/MV number. Ranges are specified below: Station Number - Range is 1 to 54 for Conventional Controllers and q to 225 for Decoder Controllers. Block Number - Range is 1 to 64. P/MV Number = Range is 1 to 6. | 000 | Av | 374 | 0x5C_Number , DA_Av ,374 ,Av ,374 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of specifie ,
0x5C | 3 | 4 | RunTime | Uint16 |  | 375 |  |  |  | Run Time for the specified device in seconds. Range is 1 to 43-200 (12 hours) for Conventional Controllers. Range is 15 to 43-200 (12 hours) for Decoder Controllrs. | 000 | Av | 375 | 0x5C_RunTime , DA_Av ,375 ,Av ,375 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Run Time for the specified device in se ,
000
0x5D – Start Multiple Manual Events | [10 empty] | 000 |  |  |  |  | 0x5D – Start Multiple Manual Events
| demo=h5d.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
| Not working | [9 empty] | 000
| Starts manual event operation. Station/Block/Pmv events may be sent, each with their own run time. Manual events may be specified to operate sequentially or simultaneously. The manual events will be inserted into the manual event table if space is available | [9 empty] | 000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x5D | 0 | 1 | Trigger_StartMultManualEvents |  | 34 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 34 | 0x5D_Trigger_StartMultManualEvents , DA_Bv ,034 ,Bv ,034 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x5D | 1 | 2 | Mode | Byte |  | 376 |  |  |  | Specifies the mode to operate the manual irrigation. 0 = Sequential. 1 = Simultaneous. | 000 | Av | 376 | 0x5D_Mode , DA_Av ,376 ,Av ,376 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Specifies the mode to operate the manua ,
0x5D | 2 | 3 | Count | Byte |  | 377 |  |  |  | Indicates the number of manual irrigation events being sent. Range is 1 to 32. | 000 | Av | 377 | 0x5D_Count , DA_Av ,377 ,Av ,377 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Indicates the number of manual irrigati ,
0x5D | 3 | 4 | EventType | Byte |  | 378 |  |  |  | Value contains the type of Event. Range is 1 to3. 1 = Station- 2 = Block- 3 = P/MV. | 000 | Av | 378 | 0x5D_EventType , DA_Av ,378 ,Av ,378 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains the type of Event. Range ,
0x5D | 4 | 5 | EventID | UINT16 |  | 379 |  |  |  | Value contains the ID of the Event Type being specified. Range is dependent upon Event Type. Station - Range is 1 to 54 for Conventional Controllers and 1 to 225 for Decoder Controllers. Block - Range is 1 to 64. P/MV - Range is 1 to 6. | 000 | Av | 379 | 0x5D_EventID , DA_Av ,379 ,Av ,379 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value contains the ID of the Event Type ,
0x5D | 5 | 6 | RunTime | UINT16 |  | 380 |  |  |  | Run time in seconds. Range is 1 to 43-200 seconds for Conventional Controllers and 15 to 43-200 seconds for Decoder Controllers. | 000 | Av | 380 | 0x5D_RunTime , DA_Av ,380 ,Av ,380 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Run time in seconds. Range is 1 to 43-2 ,
000
0x5e - 0x71 | [10 empty] | 000 |  |  |  |  | 0x5e - 0x71
| Reserved for later use by Hunter | [9 empty] | 000
000
000
000
000
0x72 – REPORT ACTIVE OUTPUTS (v2.00.025) | [10 empty] | 000 |  |  |  |  | 0x72 – REPORT ACTIVE OUTPUTS (v2.00.025)
| demo=h72.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
000
| Controller returns a list of stations that are currently running. | [9 empty] | 000
| When a response is received, the driver clears the list and then stores the fresh data. | [9 empty] | 000
000
000
000
000
000
| Data Array | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x72 | 0 | 1 | Trigger |  | 35 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 35 | 0x72_Trigger , DA_Bv ,035 ,Bv ,035 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x72 | 1 | 2 | TimeStamp | UINT32 |  |  |  | 1026 |  | Contains the time that report was cerated in Seconds After Midnight. Range is 0 to 86-399. | 000 | Ai | 1026 | 0x72_TimeStamp , DA_Ai ,1026 ,Ai ,1026 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Contains the time that report was cerat ,
0x72 | 2 | 3 | OutputCount | Byte |  |  |  | 1027 |  | The number of currently active stations. Range is 0 to 45. | 000 | Ai | 1027 | 0x72_OutputCount , DA_Ai ,1027 ,Ai ,1027 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,The number of currently active stations ,
0x72 | 3 | 4 | ActOutput 01 | UINT16 |  |  |  | 1028 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1028 | 0x72_ActOutput 01 , DA_Ai ,1028 ,Ai ,1028 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 4 | 5 | ActOutput 02 | UINT16 |  |  |  | 1029 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1029 | 0x72_ActOutput 02 , DA_Ai ,1029 ,Ai ,1029 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 5 | 6 | ActOutput 03 | UINT16 |  |  |  | 1030 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1030 | 0x72_ActOutput 03 , DA_Ai ,1030 ,Ai ,1030 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 6 | 7 | ActOutput 04 | UINT16 |  |  |  | 1031 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1031 | 0x72_ActOutput 04 , DA_Ai ,1031 ,Ai ,1031 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 7 | 8 | ActOutput 05 | UINT16 |  |  |  | 1032 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1032 | 0x72_ActOutput 05 , DA_Ai ,1032 ,Ai ,1032 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 8 | 9 | ActOutput 06 | UINT16 |  |  |  | 1033 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1033 | 0x72_ActOutput 06 , DA_Ai ,1033 ,Ai ,1033 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 9 | 10 | ActOutput 07 | UINT16 |  |  |  | 1034 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1034 | 0x72_ActOutput 07 , DA_Ai ,1034 ,Ai ,1034 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 10 | 11 | ActOutput 08 | UINT16 |  |  |  | 1035 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1035 | 0x72_ActOutput 08 , DA_Ai ,1035 ,Ai ,1035 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 11 | 12 | ActOutput 09 | UINT16 |  |  |  | 1036 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1036 | 0x72_ActOutput 09 , DA_Ai ,1036 ,Ai ,1036 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 12 | 13 | ActOutput 10 | UINT16 |  |  |  | 1037 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1037 | 0x72_ActOutput 10 , DA_Ai ,1037 ,Ai ,1037 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 13 | 14 | ActOutput 11 | UINT16 |  |  |  | 1038 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1038 | 0x72_ActOutput 11 , DA_Ai ,1038 ,Ai ,1038 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 14 | 15 | ActOutput 12 | UINT16 |  |  |  | 1039 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1039 | 0x72_ActOutput 12 , DA_Ai ,1039 ,Ai ,1039 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 15 | 16 | ActOutput 13 | UINT16 |  |  |  | 1040 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1040 | 0x72_ActOutput 13 , DA_Ai ,1040 ,Ai ,1040 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 16 | 17 | ActOutput 14 | UINT16 |  |  |  | 1041 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1041 | 0x72_ActOutput 14 , DA_Ai ,1041 ,Ai ,1041 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 17 | 18 | ActOutput 15 | UINT16 |  |  |  | 1042 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1042 | 0x72_ActOutput 15 , DA_Ai ,1042 ,Ai ,1042 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 18 | 19 | ActOutput 16 | UINT16 |  |  |  | 1043 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1043 | 0x72_ActOutput 16 , DA_Ai ,1043 ,Ai ,1043 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 19 | 20 | ActOutput 17 | UINT16 |  |  |  | 1044 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1044 | 0x72_ActOutput 17 , DA_Ai ,1044 ,Ai ,1044 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 20 | 21 | ActOutput 18 | UINT16 |  |  |  | 1045 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1045 | 0x72_ActOutput 18 , DA_Ai ,1045 ,Ai ,1045 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 21 | 22 | ActOutput 19 | UINT16 |  |  |  | 1046 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1046 | 0x72_ActOutput 19 , DA_Ai ,1046 ,Ai ,1046 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 22 | 23 | ActOutput 20 | UINT16 |  |  |  | 1047 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1047 | 0x72_ActOutput 20 , DA_Ai ,1047 ,Ai ,1047 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 23 | 24 | ActOutput 21 | UINT16 |  |  |  | 1048 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1048 | 0x72_ActOutput 21 , DA_Ai ,1048 ,Ai ,1048 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 24 | 25 | ActOutput 22 | UINT16 |  |  |  | 1049 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1049 | 0x72_ActOutput 22 , DA_Ai ,1049 ,Ai ,1049 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 25 | 26 | ActOutput 23 | UINT16 |  |  |  | 1050 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1050 | 0x72_ActOutput 23 , DA_Ai ,1050 ,Ai ,1050 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 26 | 27 | ActOutput 24 | UINT16 |  |  |  | 1051 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1051 | 0x72_ActOutput 24 , DA_Ai ,1051 ,Ai ,1051 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 27 | 28 | ActOutput 25 | UINT16 |  |  |  | 1052 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1052 | 0x72_ActOutput 25 , DA_Ai ,1052 ,Ai ,1052 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 28 | 29 | ActOutput 26 | UINT16 |  |  |  | 1053 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1053 | 0x72_ActOutput 26 , DA_Ai ,1053 ,Ai ,1053 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 29 | 30 | ActOutput 27 | UINT16 |  |  |  | 1054 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1054 | 0x72_ActOutput 27 , DA_Ai ,1054 ,Ai ,1054 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 30 | 31 | ActOutput 28 | UINT16 |  |  |  | 1055 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1055 | 0x72_ActOutput 28 , DA_Ai ,1055 ,Ai ,1055 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 31 | 32 | ActOutput 29 | UINT16 |  |  |  | 1056 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1056 | 0x72_ActOutput 29 , DA_Ai ,1056 ,Ai ,1056 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 32 | 33 | ActOutput 30 | UINT16 |  |  |  | 1057 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1057 | 0x72_ActOutput 30 , DA_Ai ,1057 ,Ai ,1057 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 33 | 34 | ActOutput 31 | UINT16 |  |  |  | 1058 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1058 | 0x72_ActOutput 31 , DA_Ai ,1058 ,Ai ,1058 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 34 | 35 | ActOutput 32 | UINT16 |  |  |  | 1059 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1059 | 0x72_ActOutput 32 , DA_Ai ,1059 ,Ai ,1059 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 35 | 36 | ActOutput 33 | UINT16 |  |  |  | 1060 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1060 | 0x72_ActOutput 33 , DA_Ai ,1060 ,Ai ,1060 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 36 | 37 | ActOutput 34 | UINT16 |  |  |  | 1061 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1061 | 0x72_ActOutput 34 , DA_Ai ,1061 ,Ai ,1061 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 37 | 38 | ActOutput 35 | UINT16 |  |  |  | 1062 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1062 | 0x72_ActOutput 35 , DA_Ai ,1062 ,Ai ,1062 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 38 | 39 | ActOutput 36 | UINT16 |  |  |  | 1063 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1063 | 0x72_ActOutput 36 , DA_Ai ,1063 ,Ai ,1063 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 39 | 40 | ActOutput 37 | UINT16 |  |  |  | 1064 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1064 | 0x72_ActOutput 37 , DA_Ai ,1064 ,Ai ,1064 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 40 | 41 | ActOutput 38 | UINT16 |  |  |  | 1065 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1065 | 0x72_ActOutput 38 , DA_Ai ,1065 ,Ai ,1065 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 41 | 42 | ActOutput 39 | UINT16 |  |  |  | 1066 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1066 | 0x72_ActOutput 39 , DA_Ai ,1066 ,Ai ,1066 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 42 | 43 | ActOutput 40 | UINT16 |  |  |  | 1067 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1067 | 0x72_ActOutput 40 , DA_Ai ,1067 ,Ai ,1067 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 43 | 44 | ActOutput 41 | UINT16 |  |  |  | 1068 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1068 | 0x72_ActOutput 41 , DA_Ai ,1068 ,Ai ,1068 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 44 | 45 | ActOutput 42 | UINT16 |  |  |  | 1069 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1069 | 0x72_ActOutput 42 , DA_Ai ,1069 ,Ai ,1069 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 45 | 46 | ActOutput 43 | UINT16 |  |  |  | 1070 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1070 | 0x72_ActOutput 43 , DA_Ai ,1070 ,Ai ,1070 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 46 | 47 | ActOutput 44 | UINT16 |  |  |  | 1071 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1071 | 0x72_ActOutput 44 , DA_Ai ,1071 ,Ai ,1071 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
0x72 | 47 | 48 | ActOutput 45 | UINT16 |  |  |  | 1072 |  | Active Output list. Present if Output Count > 0. Contains list of P/MVs and Stations that are active. Number of values returned will match value in Station Count. Valid values are as follows: 1-225 = Station Number (1 to 225). 501-506 = P/MV (1 to 6). Bits 15 – 12: Indicates mode of operation. Valid values are as follows: 0 = Normal Irrigation Mode 1 = Auxiliary Mode – Station Finder 2 = Auxiliary Mode – SOS 3 = Normal and Auxiliary Mode - SOS Bits 11 – 0: Indicates Station or P/MV Number. Valid values are as follows: 1 – 225 = Station Number (1 to 225) 501 – 506 = P/MV (1 to 6) | 000 | Ai | 1072 | 0x72_ActOutput 45 , DA_Ai ,1072 ,Ai ,1072 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Active Output list. Present if Output C ,
000
0x73 – REPORT ALARMS/INFORMATION | [10 empty] | 000 |  |  |  |  | 0x73 – REPORT ALARMS/INFORMATION
| demo=h73.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
000
| Reports alarm and information bitmaps of flags indicating the current operational status of the controller. | [9 empty] | 000
| The request does not contain a payload / params. The response data is extracted and stored as shown below. | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x73 | 0 | 1 | bit 00: Programmable Off is Active | Bit |  |  | 0 |  |  | Info Bits: Programmable Off is Active | 000 | Bi | 0 | 0x73_bit 00: Programmable Off is Active , DA_Bi ,000 ,Bi ,000 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Programmable Off is Active ,
0x73 | 1 | 2 | bit 01: Data was Reset | Bit |  |  | 1 |  |  | Info Bits: Data was Reset | 000 | Bi | 1 | 0x73_bit 01: Data was Reset , DA_Bi ,001 ,Bi ,001 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Data was Reset ,
0x73 | 2 | 3 | bit 02: | Bit |  |  | 2 |  |  | Spare | 000 | Bi | 2 | 0x73_bit 02: , DA_Bi ,002 ,Bi ,002 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Spare ,
0x73 | 3 | 4 | bit 03: Configuration was Updated | Bit |  |  | 3 |  |  | Info Bits: Configuration was Updated | 000 | Bi | 3 | 0x73_bit 03: Configuration was Updated , DA_Bi ,003 ,Bi ,003 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Configuration was Updated ,
0x73 | 4 | 5 | bit 04: Controller is Irrigating | Bit |  |  | 4 |  |  | Info Bits: Controller is Irrigating | 000 | Bi | 4 | 0x73_bit 04: Controller is Irrigating , DA_Bi ,004 ,Bi ,004 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Controller is Irrigating ,
0x73 | 5 | 6 | bit 05: Mute is Active | Bit |  |  | 5 |  |  | Info Bits: Mute is Active | 000 | Bi | 5 | 0x73_bit 05: Mute is Active , DA_Bi ,005 ,Bi ,005 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Mute is Active ,
0x73 | 6 | 7 | bit 06: Controller Suspend is Active | Bit |  |  | 6 |  |  | Info Bits: Controller Suspend is Active | 000 | Bi | 6 | 0x73_bit 06: Controller Suspend is Active , DA_Bi ,006 ,Bi ,006 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Controller Suspend is Active ,
0x73 | 7 | 8 | bit 07: Controller Pause is Active | Bit |  |  | 7 |  |  | Info Bits: Controller Pause is Active | 000 | Bi | 7 | 0x73_bit 07: Controller Pause is Active , DA_Bi ,007 ,Bi ,007 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Controller Pause is Active ,
0x73 | 8 | 9 | bit 08: | Bit |  |  | 8 |  |  | Spare | 000 | Bi | 8 | 0x73_bit 08: , DA_Bi ,008 ,Bi ,008 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Spare ,
0x73 | 9 | 10 | bit 09: | Bit |  |  | 9 |  |  | Spare | 000 | Bi | 9 | 0x73_bit 09: , DA_Bi ,009 ,Bi ,009 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Spare ,
0x73 | 10 | 11 | bit 10: | Bit |  |  | 10 |  |  | Spare | 000 | Bi | 10 | 0x73_bit 10: , DA_Bi ,010 ,Bi ,010 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Spare ,
0x73 | 11 | 12 | bit 11: Shutdown is Active | Bit |  |  | 11 |  |  | Info Bits: Shutdown is Active | 000 | Bi | 11 | 0x73_bit 11: Shutdown is Active , DA_Bi ,011 ,Bi ,011 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Shutdown is Active ,
0x73 | 12 | 13 | bit 12: Station Size Changed | Bit |  |  | 12 |  |  | Info Bits: Station Size Changed | 000 | Bi | 12 | 0x73_bit 12: Station Size Changed , DA_Bi ,012 ,Bi ,012 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Station Size Changed ,
0x73 | 13 | 14 | bit 13: Time/Date was Updated | Bit |  |  | 13 |  |  | Info Bits: Time Date was Updated | 000 | Bi | 13 | 0x73_bit 13: Time/Date was Updated , DA_Bi ,013 ,Bi ,013 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Time Date was Updated ,
0x73 | 14 | 15 | bit 14: Active Event List Full | Bit |  |  | 14 |  |  | Info Bits: Active Event List Full | 000 | Bi | 14 | 0x73_bit 14: Active Event List Full , DA_Bi ,014 ,Bi ,014 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Active Event List Full ,
0x73 | 15 | 16 | bit 15: A Program was Stopped | Bit |  |  | 15 |  |  | Info Bits: A Program was Stopped | 000 | Bi | 15 | 0x73_bit 15: A Program was Stopped , DA_Bi ,015 ,Bi ,015 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: A Program was Stopped ,
0x73 | 16 | 17 | bit 16: A Block was Stopped | Bit |  |  | 16 |  |  | Info Bits: A Block was Stopped | 000 | Bi | 16 | 0x73_bit 16: A Block was Stopped , DA_Bi ,016 ,Bi ,016 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: A Block was Stopped ,
0x73 | 17 | 18 | bit 17: A Station or PMV was Stopped | Bit |  |  | 17 |  |  | Info Bits: A Station or PMV was Stopped | 000 | Bi | 17 | 0x73_bit 17: A Station or PMV was Stopped , DA_Bi ,017 ,Bi ,017 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: A Station or PMV was Stopped ,
0x73 | 18 | 19 | bit 18: All Irrigation was Stopped | Bit |  |  | 18 |  |  | Info Bits: All Irrigation was Stopped | 000 | Bi | 18 | 0x73_bit 18: All Irrigation was Stopped , DA_Bi ,018 ,Bi ,018 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: All Irrigation was Stopped ,
0x73 | 19 | 20 | bit 19: Condition Response Statement Started | Bit |  |  | 19 |  |  | Info Bits: Condition Response Statement Started | 000 | Bi | 19 | 0x73_bit 19: Condition Response Statement Started , DA_Bi ,019 ,Bi ,019 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Condition Response Statement ,
0x73 | 20 | 21 | bit 20: Decoder Wire Test Mode Active | Bit |  |  | 20 |  |  | Info Bits: Decoder Wire Test Mode Active | 000 | Bi | 20 | 0x73_bit 20: Decoder Wire Test Mode Active , DA_Bi ,020 ,Bi ,020 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Decoder Wire Test Mode Activ ,
0x73 | 21 | 22 | bit 21: Clik Sensor is Active | Bit |  |  | 21 |  |  | Info Bits: Clik Sensor is Active | 000 | Bi | 21 | 0x73_bit 21: Clik Sensor is Active , DA_Bi ,021 ,Bi ,021 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Clik Sensor is Active ,
0x73 | 22 | 23 | bit 22: Weather Sensor is Active | Bit |  |  | 22 |  |  | Info Bits: Weather Sensor is Active | 000 | Bi | 22 | 0x73_bit 22: Weather Sensor is Active , DA_Bi ,022 ,Bi ,022 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Weather Sensor is Active ,
0x73 | 23 | 24 | bit 23: Controller Inventory Changed | Bit |  |  | 23 |  |  | Info Bits: Controller Inventory Changed | 000 | Bi | 23 | 0x73_bit 23: Controller Inventory Changed , DA_Bi ,023 ,Bi ,023 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Controller Inventory Changed ,
0x73 | 24 | 25 | bit 24: Reserved for future use | Bit |  |  | 24 |  |  | Info Bits: Reserved for future use | 000 | Bi | 24 | 0x73_bit 24: Reserved for future use , DA_Bi ,024 ,Bi ,024 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 25 | 26 | bit 25: Reserved for future use | Bit |  |  | 25 |  |  | Info Bits: Reserved for future use | 000 | Bi | 25 | 0x73_bit 25: Reserved for future use , DA_Bi ,025 ,Bi ,025 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 26 | 27 | bit 26: Reserved for future use | Bit |  |  | 26 |  |  | Info Bits: Reserved for future use | 000 | Bi | 26 | 0x73_bit 26: Reserved for future use , DA_Bi ,026 ,Bi ,026 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 27 | 28 | bit 27: Reserved for future use | Bit |  |  | 27 |  |  | Info Bits: Reserved for future use | 000 | Bi | 27 | 0x73_bit 27: Reserved for future use , DA_Bi ,027 ,Bi ,027 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 28 | 29 | bit 28: Reserved for future use | Bit |  |  | 28 |  |  | Info Bits: Reserved for future use | 000 | Bi | 28 | 0x73_bit 28: Reserved for future use , DA_Bi ,028 ,Bi ,028 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 29 | 30 | bit 29: Reserved for future use | Bit |  |  | 29 |  |  | Info Bits: Reserved for future use | 000 | Bi | 29 | 0x73_bit 29: Reserved for future use , DA_Bi ,029 ,Bi ,029 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 30 | 31 | bit 30: Reserved for future use | Bit |  |  | 30 |  |  | Info Bits: Reserved for future use | 000 | Bi | 30 | 0x73_bit 30: Reserved for future use , DA_Bi ,030 ,Bi ,030 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 31 | 32 | bit 31: Reserved for future use | Bit |  |  | 31 |  |  | Info Bits: Reserved for future use | 000 | Bi | 31 | 0x73_bit 31: Reserved for future use , DA_Bi ,031 ,Bi ,031 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Info Bits: Reserved for future use ,
0x73 | 32 | 33 | bit 00: Station Size is Zero | Bit |  |  | 32 |  |  | Alarm Bits: Station Size is Zero | 000 | Bi | 32 | 0x73_bit 00: Station Size is Zero , DA_Bi ,032 ,Bi ,032 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Station Size is Zero ,
0x73 | 33 | 34 | bit 01: Power Outage Detected | Bit |  |  | 33 |  |  | Alarm Bits: Power Outage Detected | 000 | Bi | 33 | 0x73_bit 01: Power Outage Detected , DA_Bi ,033 ,Bi ,033 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Power Outage Detected ,
0x73 | 34 | 35 | bit 02: MainSafe/Flow Zone Alarm Detected | Bit |  |  | 34 |  |  | Alarm Bits: MainSafe/Flow Zone Alarm Detected | 000 | Bi | 34 | 0x73_bit 02: MainSafe/Flow Zone Alarm Detected , DA_Bi ,034 ,Bi ,034 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: MainSafe/Flow Zone Alarm De ,
0x73 | 35 | 36 | bit 03: Clik Sensor Alarm Detected | Bit |  |  | 35 |  |  | Alarm Bits: Clik Sensor Alarm Detected | 000 | Bi | 35 | 0x73_bit 03: Clik Sensor Alarm Detected , DA_Bi ,035 ,Bi ,035 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Clik Sensor Alarm Detected ,
0x73 | 36 | 37 | bit 04: Decoder Module is Overloaded | Bit |  |  | 36 |  |  | Alarm Bits: Decoder Module is Overloaded | 000 | Bi | 36 | 0x73_bit 04: Decoder Module is Overloaded , DA_Bi ,036 ,Bi ,036 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Decoder Module is Overloade ,
0x73 | 37 | 38 | bit 05: Station Fault Detected | Bit |  |  | 37 |  |  | Alarm Bits: Station Fault Detected | 000 | Bi | 37 | 0x73_bit 05: Station Fault Detected , DA_Bi ,037 ,Bi ,037 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Station Fault Detected ,
0x73 | 38 | 39 | bit 06: P/MV Fault Detected | Bit |  |  | 38 |  |  | Alarm Bits: P/MV Fault Detected | 000 | Bi | 38 | 0x73_bit 06: P/MV Fault Detected , DA_Bi ,038 ,Bi ,038 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: P/MV Fault Detected ,
0x73 | 39 | 40 | bit 07: Weather Sensor Communications Fault Detected | Bit |  |  | 39 |  |  | Alarm Bits: Weather Sensor Communications Fault Detected | 000 | Bi | 39 | 0x73_bit 07: Weather Sensor Communications Fault Detected , DA_Bi ,039 ,Bi ,039 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Weather Sensor Communicatio ,
0x73 | 40 | 41 | bit 08: RTC Fault Detected | Bit |  |  | 40 |  |  | Alarm Bits: RTC Fault Detected | 000 | Bi | 40 | 0x73_bit 08: RTC Fault Detected , DA_Bi ,040 ,Bi ,040 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: RTC Fault Detected ,
0x73 | 41 | 42 | bit 09: Maximum Transformer Current Exceeded | Bit |  |  | 41 |  |  | Alarm Bits: Maximum Transformer Current Exceeded | 000 | Bi | 41 | 0x73_bit 09: Maximum Transformer Current Exceeded , DA_Bi ,041 ,Bi ,041 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Maximum Transformer Current ,
0x73 | 42 | 43 | bit 10: CAN Bus Fault Detected | Bit |  |  | 42 |  |  | Alarm Bits: CAN Bus Fault Detected | 000 | Bi | 42 | 0x73_bit 10: CAN Bus Fault Detected , DA_Bi ,042 ,Bi ,042 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: CAN Bus Fault Detected ,
0x73 | 43 | 44 | bit 11: Low Voltage Fault Detected | Bit |  |  | 43 |  |  | Alarm Bits: Low Voltage Fault Detected | 000 | Bi | 43 | 0x73_bit 11: Low Voltage Fault Detected , DA_Bi ,043 ,Bi ,043 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Low Voltage Fault Detected ,
0x73 | 44 | 45 | bit 12: Weather Sensor Alarm Detected | Bit |  |  | 44 |  |  | Alarm Bits: Weather Sensor Alarm Detected | 000 | Bi | 44 | 0x73_bit 12: Weather Sensor Alarm Detected , DA_Bi ,044 ,Bi ,044 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Weather Sensor Alarm Detect ,
0x73 | 45 | 46 | bit 13: Station Flow Alarm Detected | Bit |  |  | 45 |  |  | Alarm Bits: Station Flow Alarm Detected | 000 | Bi | 45 | 0x73_bit 13: Station Flow Alarm Detected , DA_Bi ,045 ,Bi ,045 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Station Flow Alarm Detected ,
0x73 | 46 | 47 | bit 14: Clik Sensor Rain Delay Alarm | Bit |  |  | 46 |  |  | Alarm Bits: Clik Sensor Rain Delay Alarm | 000 | Bi | 46 | 0x73_bit 14: Clik Sensor Rain Delay Alarm , DA_Bi ,046 ,Bi ,046 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Clik Sensor Rain Delay Alar ,
0x73 | 47 | 48 | bit 15: NWW Violation Detected | Bit |  |  | 47 |  |  | Alarm Bits: NWW Violation Detected | 000 | Bi | 47 | 0x73_bit 15: NWW Violation Detected , DA_Bi ,047 ,Bi ,047 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: NWW Violation Detected ,
0x73 | 48 | 49 | bit 16: Sensor Decoder Fault Detected | Bit |  |  | 48 |  |  | Alarm Bits: Sensor Decoder Fault Detected | 000 | Bi | 48 | 0x73_bit 16: Sensor Decoder Fault Detected , DA_Bi ,048 ,Bi ,048 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Sensor Decoder Fault Detect ,
0x73 | 49 | 50 | bit 17: Weather Sensor Rain Delay Alarm | Bit |  |  | 49 |  |  | Alarm Bits: Weather Sensor Rain Delay Alarm | 000 | Bi | 49 | 0x73_bit 17: Weather Sensor Rain Delay Alarm , DA_Bi ,049 ,Bi ,049 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Weather Sensor Rain Delay A ,
0x73 | 50 | 51 | bit 18: Reserved for future use | Bit |  |  | 50 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 50 | 0x73_bit 18: Reserved for future use , DA_Bi ,050 ,Bi ,050 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 51 | 52 | bit 19: Reserved for future use | Bit |  |  | 51 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 51 | 0x73_bit 19: Reserved for future use , DA_Bi ,051 ,Bi ,051 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 52 | 53 | bit 20: Reserved for future use | Bit |  |  | 52 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 52 | 0x73_bit 20: Reserved for future use , DA_Bi ,052 ,Bi ,052 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 53 | 54 | bit 21: Reserved for future use | Bit |  |  | 53 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 53 | 0x73_bit 21: Reserved for future use , DA_Bi ,053 ,Bi ,053 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 54 | 55 | bit 22: Reserved for future use | Bit |  |  | 54 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 54 | 0x73_bit 22: Reserved for future use , DA_Bi ,054 ,Bi ,054 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 55 | 56 | bit 23: Reserved for future use | Bit |  |  | 55 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 55 | 0x73_bit 23: Reserved for future use , DA_Bi ,055 ,Bi ,055 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 56 | 57 | bit 24: Reserved for future use | Bit |  |  | 56 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 56 | 0x73_bit 24: Reserved for future use , DA_Bi ,056 ,Bi ,056 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 57 | 58 | bit 25: Reserved for future use | Bit |  |  | 57 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 57 | 0x73_bit 25: Reserved for future use , DA_Bi ,057 ,Bi ,057 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 58 | 59 | bit 26: Reserved for future use | Bit |  |  | 58 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 58 | 0x73_bit 26: Reserved for future use , DA_Bi ,058 ,Bi ,058 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 59 | 60 | bit 27: Reserved for future use | Bit |  |  | 59 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 59 | 0x73_bit 27: Reserved for future use , DA_Bi ,059 ,Bi ,059 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 60 | 61 | bit 28: Reserved for future use | Bit |  |  | 60 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 60 | 0x73_bit 28: Reserved for future use , DA_Bi ,060 ,Bi ,060 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 61 | 62 | bit 29: Reserved for future use | Bit |  |  | 61 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 61 | 0x73_bit 29: Reserved for future use , DA_Bi ,061 ,Bi ,061 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 62 | 63 | bit 30: Reserved for future use | Bit |  |  | 62 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 62 | 0x73_bit 30: Reserved for future use , DA_Bi ,062 ,Bi ,062 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
0x73 | 63 | 64 | bit 31: Reserved for future use | Bit |  |  | 63 |  |  | Alarm Bits: Reserved for future use | 000 | Bi | 63 | 0x73_bit 31: Reserved for future use , DA_Bi ,063 ,Bi ,063 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Alarm Bits: Reserved for future use ,
000
0x74 – REPORT LOG | [10 empty] | 000 |  |  |  |  | 0x74 – REPORT LOG
| demo=h74.html | [9 empty] | 000
| Template=None | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x74 | 0 | 1 | Trigger_LogType | Byte |  | 381 |  |  |  | Trigger Cmd by selecting log type. Range is 1 to 3. 1 = Controller Log. 2= Station Log. 3 = Alarm Log. | 000 | Av | 381 | 0x74_Trigger_LogType , DA_Av ,381 ,Av ,381 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Trigger Cmd by selecting log type. Rang ,
0x74 | [9 empty] | If this value is zero then the driver uses the configuration file value of the param called -ACC2_option1- | 000
0x74 | [9 empty] | This allows this command to read specific logs or any log. | 000
0x74 | [10 empty] | 000
0x74 | 0 | 1 | LogType | Byte |  |  |  | 1073 |  | Value indicating the Log Type being requested. Range is 1 to 3. 1 = Controller Log. 2= Station Log. 3 = Alarm Log. | 000 | Ai | 1073 | 0x74_LogType , DA_Ai ,1073 ,Ai ,1073 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Log Type being req ,
0x74 | 1 | 2 | LogCount | Byte |  |  |  | 1074 |  | Number of logs in this transmission. 0 indicates no logs available. Range is 0 to 20. | 000 | Ai | 1074 | 0x74_LogCount , DA_Ai ,1074 ,Ai ,1074 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Number of logs in this transmission. 0 ,
0x74 | 2 | 3 | UnixTime | UINT32 |  |  |  | 1075 | Rec01 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1075 | 0x74_Rec01UnixTime , DA_Ai ,1075 ,Ai ,1075 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 3 | 4 | Idiom | Byte |  |  |  | 1076 | Rec01 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1076 | 0x74_Rec01Idiom , DA_Ai ,1076 ,Ai ,1076 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 4 | 5 | Field1 | Byte |  |  |  | 1077 | Rec01 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1077 | 0x74_Rec01Field1 , DA_Ai ,1077 ,Ai ,1077 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 5 | 6 | Field2 | UINT16 |  |  |  | 1078 | Rec01 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1078 | 0x74_Rec01Field2 , DA_Ai ,1078 ,Ai ,1078 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 6 | 7 | Field3 | UINT16 |  |  |  | 1079 | Rec01 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1079 | 0x74_Rec01Field3 , DA_Ai ,1079 ,Ai ,1079 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 7 | 8 | Field4 | UINT16 |  |  |  | 1080 | Rec01 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1080 | 0x74_Rec01Field4 , DA_Ai ,1080 ,Ai ,1080 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 8 | 9 | UnixTime | UINT32 |  |  |  | 1081 | Rec02 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1081 | 0x74_Rec02UnixTime , DA_Ai ,1081 ,Ai ,1081 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 9 | 10 | Idiom | Byte |  |  |  | 1082 | Rec02 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1082 | 0x74_Rec02Idiom , DA_Ai ,1082 ,Ai ,1082 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 10 | 11 | Field1 | Byte |  |  |  | 1083 | Rec02 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1083 | 0x74_Rec02Field1 , DA_Ai ,1083 ,Ai ,1083 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 11 | 12 | Field2 | UINT16 |  |  |  | 1084 | Rec02 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1084 | 0x74_Rec02Field2 , DA_Ai ,1084 ,Ai ,1084 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 12 | 13 | Field3 | UINT16 |  |  |  | 1085 | Rec02 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1085 | 0x74_Rec02Field3 , DA_Ai ,1085 ,Ai ,1085 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 13 | 14 | Field4 | UINT16 |  |  |  | 1086 | Rec02 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1086 | 0x74_Rec02Field4 , DA_Ai ,1086 ,Ai ,1086 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 14 | 15 | UnixTime | UINT32 |  |  |  | 1087 | Rec03 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1087 | 0x74_Rec03UnixTime , DA_Ai ,1087 ,Ai ,1087 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 15 | 16 | Idiom | Byte |  |  |  | 1088 | Rec03 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1088 | 0x74_Rec03Idiom , DA_Ai ,1088 ,Ai ,1088 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 16 | 17 | Field1 | Byte |  |  |  | 1089 | Rec03 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1089 | 0x74_Rec03Field1 , DA_Ai ,1089 ,Ai ,1089 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 17 | 18 | Field2 | UINT16 |  |  |  | 1090 | Rec03 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1090 | 0x74_Rec03Field2 , DA_Ai ,1090 ,Ai ,1090 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 18 | 19 | Field3 | UINT16 |  |  |  | 1091 | Rec03 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1091 | 0x74_Rec03Field3 , DA_Ai ,1091 ,Ai ,1091 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 19 | 20 | Field4 | UINT16 |  |  |  | 1092 | Rec03 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1092 | 0x74_Rec03Field4 , DA_Ai ,1092 ,Ai ,1092 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 20 | 21 | UnixTime | UINT32 |  |  |  | 1093 | Rec04 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1093 | 0x74_Rec04UnixTime , DA_Ai ,1093 ,Ai ,1093 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 21 | 22 | Idiom | Byte |  |  |  | 1094 | Rec04 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1094 | 0x74_Rec04Idiom , DA_Ai ,1094 ,Ai ,1094 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 22 | 23 | Field1 | Byte |  |  |  | 1095 | Rec04 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1095 | 0x74_Rec04Field1 , DA_Ai ,1095 ,Ai ,1095 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 23 | 24 | Field2 | UINT16 |  |  |  | 1096 | Rec04 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1096 | 0x74_Rec04Field2 , DA_Ai ,1096 ,Ai ,1096 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 24 | 25 | Field3 | UINT16 |  |  |  | 1097 | Rec04 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1097 | 0x74_Rec04Field3 , DA_Ai ,1097 ,Ai ,1097 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 25 | 26 | Field4 | UINT16 |  |  |  | 1098 | Rec04 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1098 | 0x74_Rec04Field4 , DA_Ai ,1098 ,Ai ,1098 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 26 | 27 | LogType | Byte |  |  |  | 1099 | Rec05 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1099 | 0x74_Rec05LogType , DA_Ai ,1099 ,Ai ,1099 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 27 | 28 | LogCount | Byte |  |  |  | 1100 | Rec05 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1100 | 0x74_Rec05LogCount , DA_Ai ,1100 ,Ai ,1100 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 28 | 29 | UnixTime | UINT32 |  |  |  | 1101 | Rec05 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1101 | 0x74_Rec05UnixTime , DA_Ai ,1101 ,Ai ,1101 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 29 | 30 | Idiom | Byte |  |  |  | 1102 | Rec05 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1102 | 0x74_Rec05Idiom , DA_Ai ,1102 ,Ai ,1102 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 30 | 31 | Field1 | Byte |  |  |  | 1103 | Rec05 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1103 | 0x74_Rec05Field1 , DA_Ai ,1103 ,Ai ,1103 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 31 | 32 | Field2 | UINT16 |  |  |  | 1104 | Rec05 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1104 | 0x74_Rec05Field2 , DA_Ai ,1104 ,Ai ,1104 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 32 | 33 | Field3 | UINT16 |  |  |  | 1105 | Rec06 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1105 | 0x74_Rec06Field3 , DA_Ai ,1105 ,Ai ,1105 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 33 | 34 | Field4 | UINT16 |  |  |  | 1106 | Rec06 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1106 | 0x74_Rec06Field4 , DA_Ai ,1106 ,Ai ,1106 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 34 | 35 | UnixTime | UINT32 |  |  |  | 1107 | Rec06 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1107 | 0x74_Rec06UnixTime , DA_Ai ,1107 ,Ai ,1107 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 35 | 36 | Idiom | Byte |  |  |  | 1108 | Rec06 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1108 | 0x74_Rec06Idiom , DA_Ai ,1108 ,Ai ,1108 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 36 | 37 | Field1 | Byte |  |  |  | 1109 | Rec06 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1109 | 0x74_Rec06Field1 , DA_Ai ,1109 ,Ai ,1109 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 37 | 38 | Field2 | UINT16 |  |  |  | 1110 | Rec06 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1110 | 0x74_Rec06Field2 , DA_Ai ,1110 ,Ai ,1110 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 38 | 39 | Field3 | UINT16 |  |  |  | 1111 | Rec07 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1111 | 0x74_Rec07Field3 , DA_Ai ,1111 ,Ai ,1111 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 39 | 40 | Field4 | UINT16 |  |  |  | 1112 | Rec07 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1112 | 0x74_Rec07Field4 , DA_Ai ,1112 ,Ai ,1112 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 40 | 41 | UnixTime | UINT32 |  |  |  | 1113 | Rec07 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1113 | 0x74_Rec07UnixTime , DA_Ai ,1113 ,Ai ,1113 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 41 | 42 | Idiom | Byte |  |  |  | 1114 | Rec07 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1114 | 0x74_Rec07Idiom , DA_Ai ,1114 ,Ai ,1114 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 42 | 43 | Field1 | Byte |  |  |  | 1115 | Rec07 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1115 | 0x74_Rec07Field1 , DA_Ai ,1115 ,Ai ,1115 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 43 | 44 | Field2 | UINT16 |  |  |  | 1116 | Rec07 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1116 | 0x74_Rec07Field2 , DA_Ai ,1116 ,Ai ,1116 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 44 | 45 | Field3 | UINT16 |  |  |  | 1117 | Rec08 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1117 | 0x74_Rec08Field3 , DA_Ai ,1117 ,Ai ,1117 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 45 | 46 | Field4 | UINT16 |  |  |  | 1118 | Rec08 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1118 | 0x74_Rec08Field4 , DA_Ai ,1118 ,Ai ,1118 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 46 | 47 | UnixTime | UINT32 |  |  |  | 1119 | Rec08 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1119 | 0x74_Rec08UnixTime , DA_Ai ,1119 ,Ai ,1119 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 47 | 48 | Idiom | Byte |  |  |  | 1120 | Rec08 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1120 | 0x74_Rec08Idiom , DA_Ai ,1120 ,Ai ,1120 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 48 | 49 | Field1 | Byte |  |  |  | 1121 | Rec08 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1121 | 0x74_Rec08Field1 , DA_Ai ,1121 ,Ai ,1121 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 49 | 50 | Field2 | UINT16 |  |  |  | 1122 | Rec08 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1122 | 0x74_Rec08Field2 , DA_Ai ,1122 ,Ai ,1122 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 50 | 51 | Field3 | UINT16 |  |  |  | 1123 | Rec09 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1123 | 0x74_Rec09Field3 , DA_Ai ,1123 ,Ai ,1123 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 51 | 52 | Field4 | UINT16 |  |  |  | 1124 | Rec09 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1124 | 0x74_Rec09Field4 , DA_Ai ,1124 ,Ai ,1124 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 52 | 53 | LogType | Byte |  |  |  | 1125 | Rec09 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1125 | 0x74_Rec09LogType , DA_Ai ,1125 ,Ai ,1125 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 53 | 54 | LogCount | Byte |  |  |  | 1126 | Rec09 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1126 | 0x74_Rec09LogCount , DA_Ai ,1126 ,Ai ,1126 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 54 | 55 | UnixTime | UINT32 |  |  |  | 1127 | Rec09 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1127 | 0x74_Rec09UnixTime , DA_Ai ,1127 ,Ai ,1127 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 55 | 56 | Idiom | Byte |  |  |  | 1128 | Rec09 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1128 | 0x74_Rec09Idiom , DA_Ai ,1128 ,Ai ,1128 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 56 | 57 | Field1 | Byte |  |  |  | 1129 | Rec10 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1129 | 0x74_Rec10Field1 , DA_Ai ,1129 ,Ai ,1129 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 57 | 58 | Field2 | UINT16 |  |  |  | 1130 | Rec10 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1130 | 0x74_Rec10Field2 , DA_Ai ,1130 ,Ai ,1130 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 58 | 59 | Field3 | UINT16 |  |  |  | 1131 | Rec10 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1131 | 0x74_Rec10Field3 , DA_Ai ,1131 ,Ai ,1131 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 59 | 60 | Field4 | UINT16 |  |  |  | 1132 | Rec10 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1132 | 0x74_Rec10Field4 , DA_Ai ,1132 ,Ai ,1132 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 60 | 61 | UnixTime | UINT32 |  |  |  | 1133 | Rec10 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1133 | 0x74_Rec10UnixTime , DA_Ai ,1133 ,Ai ,1133 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 61 | 62 | Idiom | Byte |  |  |  | 1134 | Rec10 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1134 | 0x74_Rec10Idiom , DA_Ai ,1134 ,Ai ,1134 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 62 | 63 | Field1 | Byte |  |  |  | 1135 | Rec11 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1135 | 0x74_Rec11Field1 , DA_Ai ,1135 ,Ai ,1135 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 63 | 64 | Field2 | UINT16 |  |  |  | 1136 | Rec11 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1136 | 0x74_Rec11Field2 , DA_Ai ,1136 ,Ai ,1136 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 64 | 65 | Field3 | UINT16 |  |  |  | 1137 | Rec11 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1137 | 0x74_Rec11Field3 , DA_Ai ,1137 ,Ai ,1137 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 65 | 66 | Field4 | UINT16 |  |  |  | 1138 | Rec11 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1138 | 0x74_Rec11Field4 , DA_Ai ,1138 ,Ai ,1138 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 66 | 67 | UnixTime | UINT32 |  |  |  | 1139 | Rec11 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1139 | 0x74_Rec11UnixTime , DA_Ai ,1139 ,Ai ,1139 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 67 | 68 | Idiom | Byte |  |  |  | 1140 | Rec11 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1140 | 0x74_Rec11Idiom , DA_Ai ,1140 ,Ai ,1140 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 68 | 69 | Field1 | Byte |  |  |  | 1141 | Rec12 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1141 | 0x74_Rec12Field1 , DA_Ai ,1141 ,Ai ,1141 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 69 | 70 | Field2 | UINT16 |  |  |  | 1142 | Rec12 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1142 | 0x74_Rec12Field2 , DA_Ai ,1142 ,Ai ,1142 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 70 | 71 | Field3 | UINT16 |  |  |  | 1143 | Rec12 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1143 | 0x74_Rec12Field3 , DA_Ai ,1143 ,Ai ,1143 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 71 | 72 | Field4 | UINT16 |  |  |  | 1144 | Rec12 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1144 | 0x74_Rec12Field4 , DA_Ai ,1144 ,Ai ,1144 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 72 | 73 | UnixTime | UINT32 |  |  |  | 1145 | Rec12 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1145 | 0x74_Rec12UnixTime , DA_Ai ,1145 ,Ai ,1145 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 73 | 74 | Idiom | Byte |  |  |  | 1146 | Rec12 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1146 | 0x74_Rec12Idiom , DA_Ai ,1146 ,Ai ,1146 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 74 | 75 | Field1 | Byte |  |  |  | 1147 | Rec13 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1147 | 0x74_Rec13Field1 , DA_Ai ,1147 ,Ai ,1147 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 75 | 76 | Field2 | UINT16 |  |  |  | 1148 | Rec13 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1148 | 0x74_Rec13Field2 , DA_Ai ,1148 ,Ai ,1148 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 76 | 77 | Field3 | UINT16 |  |  |  | 1149 | Rec13 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1149 | 0x74_Rec13Field3 , DA_Ai ,1149 ,Ai ,1149 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 77 | 78 | Field4 | UINT16 |  |  |  | 1150 | Rec13 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1150 | 0x74_Rec13Field4 , DA_Ai ,1150 ,Ai ,1150 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 78 | 79 | LogType | Byte |  |  |  | 1151 | Rec13 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1151 | 0x74_Rec13LogType , DA_Ai ,1151 ,Ai ,1151 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 79 | 80 | LogCount | Byte |  |  |  | 1152 | Rec13 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1152 | 0x74_Rec13LogCount , DA_Ai ,1152 ,Ai ,1152 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 80 | 81 | UnixTime | UINT32 |  |  |  | 1153 | Rec14 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1153 | 0x74_Rec14UnixTime , DA_Ai ,1153 ,Ai ,1153 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 81 | 82 | Idiom | Byte |  |  |  | 1154 | Rec14 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1154 | 0x74_Rec14Idiom , DA_Ai ,1154 ,Ai ,1154 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 82 | 83 | Field1 | Byte |  |  |  | 1155 | Rec14 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1155 | 0x74_Rec14Field1 , DA_Ai ,1155 ,Ai ,1155 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 83 | 84 | Field2 | UINT16 |  |  |  | 1156 | Rec14 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1156 | 0x74_Rec14Field2 , DA_Ai ,1156 ,Ai ,1156 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 84 | 85 | Field3 | UINT16 |  |  |  | 1157 | Rec14 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1157 | 0x74_Rec14Field3 , DA_Ai ,1157 ,Ai ,1157 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 85 | 86 | Field4 | UINT16 |  |  |  | 1158 | Rec14 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1158 | 0x74_Rec14Field4 , DA_Ai ,1158 ,Ai ,1158 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 86 | 87 | UnixTime | UINT32 |  |  |  | 1159 | Rec15 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1159 | 0x74_Rec15UnixTime , DA_Ai ,1159 ,Ai ,1159 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 87 | 88 | Idiom | Byte |  |  |  | 1160 | Rec15 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1160 | 0x74_Rec15Idiom , DA_Ai ,1160 ,Ai ,1160 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 88 | 89 | Field1 | Byte |  |  |  | 1161 | Rec15 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1161 | 0x74_Rec15Field1 , DA_Ai ,1161 ,Ai ,1161 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 89 | 90 | Field2 | UINT16 |  |  |  | 1162 | Rec15 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1162 | 0x74_Rec15Field2 , DA_Ai ,1162 ,Ai ,1162 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 90 | 91 | Field3 | UINT16 |  |  |  | 1163 | Rec15 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1163 | 0x74_Rec15Field3 , DA_Ai ,1163 ,Ai ,1163 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 91 | 92 | Field4 | UINT16 |  |  |  | 1164 | Rec15 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1164 | 0x74_Rec15Field4 , DA_Ai ,1164 ,Ai ,1164 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 92 | 93 | UnixTime | UINT32 |  |  |  | 1165 | Rec16 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1165 | 0x74_Rec16UnixTime , DA_Ai ,1165 ,Ai ,1165 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 93 | 94 | Idiom | Byte |  |  |  | 1166 | Rec16 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1166 | 0x74_Rec16Idiom , DA_Ai ,1166 ,Ai ,1166 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 94 | 95 | Field1 | Byte |  |  |  | 1167 | Rec16 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1167 | 0x74_Rec16Field1 , DA_Ai ,1167 ,Ai ,1167 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 95 | 96 | Field2 | UINT16 |  |  |  | 1168 | Rec16 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1168 | 0x74_Rec16Field2 , DA_Ai ,1168 ,Ai ,1168 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 96 | 97 | Field3 | UINT16 |  |  |  | 1169 | Rec16 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1169 | 0x74_Rec16Field3 , DA_Ai ,1169 ,Ai ,1169 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 97 | 98 | Field4 | UINT16 |  |  |  | 1170 | Rec16 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1170 | 0x74_Rec16Field4 , DA_Ai ,1170 ,Ai ,1170 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 98 | 99 | UnixTime | UINT32 |  |  |  | 1171 | Rec17 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1171 | 0x74_Rec17UnixTime , DA_Ai ,1171 ,Ai ,1171 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 99 | 100 | Idiom | Byte |  |  |  | 1172 | Rec17 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1172 | 0x74_Rec17Idiom , DA_Ai ,1172 ,Ai ,1172 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 100 | 101 | Field1 | Byte |  |  |  | 1173 | Rec17 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1173 | 0x74_Rec17Field1 , DA_Ai ,1173 ,Ai ,1173 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 101 | 102 | Field2 | UINT16 |  |  |  | 1174 | Rec17 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1174 | 0x74_Rec17Field2 , DA_Ai ,1174 ,Ai ,1174 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 102 | 103 | Field3 | UINT16 |  |  |  | 1175 | Rec17 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1175 | 0x74_Rec17Field3 , DA_Ai ,1175 ,Ai ,1175 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 103 | 104 | Field4 | UINT16 |  |  |  | 1176 | Rec17 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1176 | 0x74_Rec17Field4 , DA_Ai ,1176 ,Ai ,1176 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 104 | 105 | LogType | Byte |  |  |  | 1177 | Rec18 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1177 | 0x74_Rec18LogType , DA_Ai ,1177 ,Ai ,1177 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 105 | 106 | LogCount | Byte |  |  |  | 1178 | Rec18 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1178 | 0x74_Rec18LogCount , DA_Ai ,1178 ,Ai ,1178 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 106 | 107 | UnixTime | UINT32 |  |  |  | 1179 | Rec18 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1179 | 0x74_Rec18UnixTime , DA_Ai ,1179 ,Ai ,1179 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 107 | 108 | Idiom | Byte |  |  |  | 1180 | Rec18 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1180 | 0x74_Rec18Idiom , DA_Ai ,1180 ,Ai ,1180 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 108 | 109 | Field1 | Byte |  |  |  | 1181 | Rec18 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1181 | 0x74_Rec18Field1 , DA_Ai ,1181 ,Ai ,1181 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 109 | 110 | Field2 | UINT16 |  |  |  | 1182 | Rec18 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1182 | 0x74_Rec18Field2 , DA_Ai ,1182 ,Ai ,1182 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 110 | 111 | Field3 | UINT16 |  |  |  | 1183 | Rec19 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1183 | 0x74_Rec19Field3 , DA_Ai ,1183 ,Ai ,1183 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 111 | 112 | Field4 | UINT16 |  |  |  | 1184 | Rec19 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1184 | 0x74_Rec19Field4 , DA_Ai ,1184 ,Ai ,1184 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 112 | 113 | UnixTime | UINT32 |  |  |  | 1185 | Rec19 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1185 | 0x74_Rec19UnixTime , DA_Ai ,1185 ,Ai ,1185 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 113 | 114 | Idiom | Byte |  |  |  | 1186 | Rec19 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1186 | 0x74_Rec19Idiom , DA_Ai ,1186 ,Ai ,1186 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 114 | 115 | Field1 | Byte |  |  |  | 1187 | Rec19 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1187 | 0x74_Rec19Field1 , DA_Ai ,1187 ,Ai ,1187 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 115 | 116 | Field2 | UINT16 |  |  |  | 1188 | Rec19 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1188 | 0x74_Rec19Field2 , DA_Ai ,1188 ,Ai ,1188 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 116 | 117 | Field3 | UINT16 |  |  |  | 1189 | Rec20 | Unsigned value representing the Unic Time when log record was generated. | 000 | Ai | 1189 | 0x74_Rec20Field3 , DA_Ai ,1189 ,Ai ,1189 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unsigned value representing the Unic Ti ,
0x74 | 117 | 118 | Field4 | UINT16 |  |  |  | 1190 | Rec20 | Value containing descriptor of what type of event was logged. | 000 | Ai | 1190 | 0x74_Rec20Field4 , DA_Ai ,1190 ,Ai ,1190 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value containing descriptor of what typ ,
0x74 | 118 | 119 | UnixTime | UINT32 |  |  |  | 1191 | Rec20 | Controller Log: Value contraining source of the event generating the log record. Station Log: Value containing the Reason for the station log record. Alarm Log: Value containing reason for log entry. | 000 | Ai | 1191 | 0x74_Rec20UnixTime , DA_Ai ,1191 ,Ai ,1191 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value contraining sourc ,
0x74 | 119 | 120 | Idiom | Byte |  |  |  | 1192 | Rec20 | Controller Log: Not used in Controller Log. Alarm Log: Value containing miscellaneous information. Station Log: Bitmapped value containing Station or P/MV Number and Block Number of running event. | 000 | Ai | 1192 | 0x74_Rec20Idiom , DA_Ai ,1192 ,Ai ,1192 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Not used in Controller ,
0x74 | 120 | 121 | Field1 | Byte |  |  |  | 1193 | Rec20 | Controller Log: Value containing miscellaneous information. May be Station Number- Program Number etc. Station Log: Value containing Run Time information. May be time a station ran- time spent in delay or pause. Alarm Log: Not used. | 000 | Ai | 1193 | 0x74_Rec20Field1 , DA_Ai ,1193 ,Ai ,1193 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
0x74 | 121 | 122 | Field2 | UINT16 |  |  |  | 1194 | Rec20 | Controller Log: Value containing miscellaneous information. May be count- time value- etc. Station Log: Bitmapped value containing event information on how station was running. Alarm Log: Value containing miscellaneous information. May be a sensor number- etc. | 000 | Ai | 1194 | 0x74_Rec20Field2 , DA_Ai ,1194 ,Ai ,1194 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Controller Log: Value containing miscel ,
000
0x75 – REPORT CURRENT FLOW DATA | [10 empty] | 000 |  |  |  |  | 0x75 – REPORT CURRENT FLOW DATA
| demo=h75.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
| This command will report current flow rate for each of the 6 Flow Sensors in the controller. | [9 empty] | 000
| This request does not carry a payload. The data in the response is extracted and stored as shown below. | [9 empty] | 000
000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x75 | 0 | 1 | FSen1Freq | UINT16 |  |  |  | 1195 |  | Value indicating the current frequency in Hz for the Flow Sensor. | 000 | Ai | 1195 | 0x75_FSen1Freq , DA_Ai ,1195 ,Ai ,1195 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current frequency ,
0x75 | 1 | 2 | FSen1FlowRate | UINT32 |  |  |  | 1196 |  | Value indicating the current flow rate times 10 in GPM for the Flow Sensor | 000 | Ai | 1196 | 0x75_FSen1FlowRate , DA_Ai ,1196 ,Ai ,1196 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current flow rate ,
0x75 | 2 | 3 | FSen2Freq | UINT16 |  |  |  | 1197 |  | Value indicating the current frequency in Hz for the Flow Sensor. | 000 | Ai | 1197 | 0x75_FSen2Freq , DA_Ai ,1197 ,Ai ,1197 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current frequency ,
0x75 | 3 | 4 | FSen2FlowRate | UINT32 |  |  |  | 1198 |  | Value indicating the current flow rate times 10 in GPM for the Flow Sensor | 000 | Ai | 1198 | 0x75_FSen2FlowRate , DA_Ai ,1198 ,Ai ,1198 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current flow rate ,
0x75 | 4 | 5 | FSen3Freq | UINT16 |  |  |  | 1199 |  | Value indicating the current frequency in Hz for the Flow Sensor. | 000 | Ai | 1199 | 0x75_FSen3Freq , DA_Ai ,1199 ,Ai ,1199 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current frequency ,
0x75 | 5 | 6 | FSen3FlowRate | UINT32 |  |  |  | 1200 |  | Value indicating the current flow rate times 10 in GPM for the Flow Sensor | 000 | Ai | 1200 | 0x75_FSen3FlowRate , DA_Ai ,1200 ,Ai ,1200 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current flow rate ,
0x75 | 6 | 7 | FSen4Freq | UINT16 |  |  |  | 1201 |  | Value indicating the current frequency in Hz for the Flow Sensor. | 000 | Ai | 1201 | 0x75_FSen4Freq , DA_Ai ,1201 ,Ai ,1201 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current frequency ,
0x75 | 7 | 8 | FSen4FlowRate | UINT32 |  |  |  | 1202 |  | Value indicating the current flow rate times 10 in GPM for the Flow Sensor | 000 | Ai | 1202 | 0x75_FSen4FlowRate , DA_Ai ,1202 ,Ai ,1202 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current flow rate ,
0x75 | 8 | 9 | FSen5Freq | UINT16 |  |  |  | 1203 |  | Value indicating the current frequency in Hz for the Flow Sensor. | 000 | Ai | 1203 | 0x75_FSen5Freq , DA_Ai ,1203 ,Ai ,1203 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current frequency ,
0x75 | 9 | 10 | FSen5FlowRate | UINT32 |  |  |  | 1204 |  | Value indicating the current flow rate times 10 in GPM for the Flow Sensor | 000 | Ai | 1204 | 0x75_FSen5FlowRate , DA_Ai ,1204 ,Ai ,1204 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current flow rate ,
0x75 | 10 | 11 | FSen6Freq | UINT16 |  |  |  | 1205 |  | Value indicating the current frequency in Hz for the Flow Sensor. | 000 | Ai | 1205 | 0x75_FSen6Freq , DA_Ai ,1205 ,Ai ,1205 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current frequency ,
0x75 | 11 | 12 | Fsen6FlowRate | UINT32 |  |  |  | 1206 |  | Value indicating the current flow rate times 10 in GPM for the Flow Sensor | 000 | Ai | 1206 | 0x75_Fsen6FlowRate , DA_Ai ,1206 ,Ai ,1206 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current flow rate ,
000
0x76 – REPORT CLIK SENSOR INFORMATION | [10 empty] | 000 |  |  |  |  | 0x76 – REPORT CLIK SENSOR INFORMATION
| demo=h76.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
000
| This command will report current sensor state and active status for all Clik sensors in the controller. The state indicates whether the sensor is open or closed and the active status is based on the current state vs. the configured normal state. | [9 empty] | 000
| This request does not carry a payload. The data in the response is extracted and stored as shown below. | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x76 | 0 | 1 | Clik1State | Byte |  |  |  | 1207 |  | Value indicating the current state of the Clik X sensor. Range is 0 to 2. 0 = Unknown. 1 = Closed. 2 = Open. | 000 | Ai | 1207 | 0x76_Clik1State , DA_Ai ,1207 ,Ai ,1207 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current state of t ,
0x76 | 1 | 2 | Clik1Active | Byte |  |  |  | 1208 |  | Value indicating whether the Clik X sensor is in an active condition baed on its configuration. Range is 0 to 1. 0 = Not active. 1 = Active. | 000 | Ai | 1208 | 0x76_Clik1Active , DA_Ai ,1208 ,Ai ,1208 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether the Clik X sen ,
0x76 | 2 | 3 | Clik2State | Byte |  |  |  | 1209 |  | Value indicating the current state of the Clik X sensor. Range is 0 to 2. 0 = Unknown. 1 = Closed. 2 = Open. | 000 | Ai | 1209 | 0x76_Clik2State , DA_Ai ,1209 ,Ai ,1209 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current state of t ,
0x76 | 3 | 4 | Clik2Active | Byte |  |  |  | 1210 |  | Value indicating whether the Clik X sensor is in an active condition baed on its configuration. Range is 0 to 1. 0 = Not active. 1 = Active. | 000 | Ai | 1210 | 0x76_Clik2Active , DA_Ai ,1210 ,Ai ,1210 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether the Clik X sen ,
0x76 | 4 | 5 | Clik3State | Byte |  |  |  | 1211 |  | Value indicating the current state of the Clik X sensor. Range is 0 to 2. 0 = Unknown. 1 = Closed. 2 = Open. | 000 | Ai | 1211 | 0x76_Clik3State , DA_Ai ,1211 ,Ai ,1211 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the current state of t ,
0x76 | 5 | 6 | Clik3Active | Byte |  |  |  | 1212 |  | Value indicating whether the Clik X sensor is in an active condition baed on its configuration. Range is 0 to 1. 0 = Not active. 1 = Active. | 000 | Ai | 1212 | 0x76_Clik3Active , DA_Ai ,1212 ,Ai ,1212 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether the Clik X sen ,
000
0x77 – REPORT DECODER MODULE INFORMATION (v2.00.024 and later) | [10 empty] | 000 |  |  |  |  | 0x77 – REPORT DECODER MODULE INFORMATION (v2.00.024 and later)
| demo=h77.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
000
| This command will report information on each of the Decoder Modules of the Decoder Controller. Information includes whether the module is installed, overload status, watering status and latest current reading. | [9 empty] | 000
| This request does not carry a payload. The data in the response is extracted and stored as shown below. | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x77 | 0 | 1 | DecModNum | Byte |  |  |  | 1213 | DecMod1 | Decoder Module Number reporting information. Range is 1 to 3. | 000 | Ai | 1213 | 0x77_DecMod1DecModNum , DA_Ai ,1213 ,Ai ,1213 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module Number reporting informa ,
0x77 | 1 | 2 | Installed | Byte |  |  |  | 1214 | DecMod1 | Decoder Module is installed. If module is not installed then all remaining bytes for the module will be 0 and should be ignored. Range is 0 to 1. 0 = Not Installed. 1 = Installed. | 000 | Ai | 1214 | 0x77_DecMod1Installed , DA_Ai ,1214 ,Ai ,1214 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module is installed. If module ,
0x77 | 2 | 3 | PathStatus | Byte |  |  |  | 1215 | DecMod1 | Status of the 2-wire path. Range is 0 to 1. 0 = 2-wire path is off. 1 = 2-wire path is on. | 000 | Ai | 1215 | 0x77_DecMod1PathStatus , DA_Ai ,1215 ,Ai ,1215 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Status of the 2-wire path. Range is 0 t ,
0x77 | 3 | 4 | OutputMode | Byte |  |  |  | 1216 | DecMod1 | Output mode of the 2-wire path. Range 0 to 1. 0 = Normal output mode. 1 = Wire test mode (60Hz). | 000 | Ai | 1216 | 0x77_DecMod1OutputMode , DA_Ai ,1216 ,Ai ,1216 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Output mode of the 2-wire path. Range 0 ,
0x77 | 4 | 5 | WaterngStatus | Byte |  |  |  | 1217 | DecMod1 | Watering status. Range is 0 to 1. 0 = Module is not watering. 1 = Module is watering. | 000 | Ai | 1217 | 0x77_DecMod1WaterngStatus , DA_Ai ,1217 ,Ai ,1217 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Watering status. Range is 0 to 1. 0 = M ,
0x77 | 5 | 6 | OverloadStatus | Byte |  |  |  | 1218 | DecMod1 | Overload status. Range is 0 to 1. 0 = Module is not overloaded. 1 = Module is overloaded. | 000 | Ai | 1218 | 0x77_DecMod1OverloadStatus , DA_Ai ,1218 ,Ai ,1218 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Overload status. Range is 0 to 1. 0 = M ,
0x77 | 6 | 7 | A/DFullScale | Byte |  |  |  | 1219 | DecMod1 | A2D is at full scale. Value is only valid if module is overloaded. Range is 0 to 1. 0 = A/D is not full scale. 1 = A/D is full scale. | 000 | Ai | 1219 | 0x77_DecMod1A/DFullScale , DA_Ai ,1219 ,Ai ,1219 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,A2D is at full scale. Value is only val ,
0x77 | 7 | 8 | Ph1/2Mismatch | Byte |  |  |  | 1220 | DecMod1 | Phase 1/2 mismatch. Value is only valid if module is overloaded. Range is 0 to 1. 0 = Phase 1/2 is not mismatched. 1 = Phase 1/2 is mismatched. | 000 | Ai | 1220 | 0x77_DecMod1Ph1/2Mismatch , DA_Ai ,1220 ,Ai ,1220 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Phase 1/2 mismatch. Value is only valid ,
0x77 | 8 | 9 | LockOutTime | UINT16 |  |  |  | 1221 | DecMod1 | Seconds remaining if the Decoder Module has been locked out by the Facepakc due to ongoing overloads. Value is only valid module is overloaded. Valid values are 0 to 3600. | 000 | Ai | 1221 | 0x77_DecMod1LockOutTime , DA_Ai ,1221 ,Ai ,1221 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds remaining if the Decoder Module ,
0x77 | 9 | 10 | DecModNum | Byte |  |  |  | 1222 | DecMod2 | Decoder Module Number reporting information. Range is 1 to 3. | 000 | Ai | 1222 | 0x77_DecMod2DecModNum , DA_Ai ,1222 ,Ai ,1222 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module Number reporting informa ,
0x77 | 10 | 11 | Installed | Byte |  |  |  | 1223 | DecMod2 | Decoder Module is installed. If module is not installed then all remaining bytes for the module will be 0 and should be ignored. Range is 0 to 1. 0 = Not Installed. 1 = Installed. | 000 | Ai | 1223 | 0x77_DecMod2Installed , DA_Ai ,1223 ,Ai ,1223 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module is installed. If module ,
0x77 | 11 | 12 | PathStatus | Byte |  |  |  | 1224 | DecMod2 | Status of the 2-wire path. Range is 0 to 1. 0 = 2-wire path is off. 1 = 2-wire path is on. | 000 | Ai | 1224 | 0x77_DecMod2PathStatus , DA_Ai ,1224 ,Ai ,1224 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Status of the 2-wire path. Range is 0 t ,
0x77 | 12 | 13 | OutputMode | Byte |  |  |  | 1225 | DecMod2 | Output mode of the 2-wire path. Range 0 to 1. 0 = Normal output mode. 1 = Wire test mode (60Hz). | 000 | Ai | 1225 | 0x77_DecMod2OutputMode , DA_Ai ,1225 ,Ai ,1225 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Output mode of the 2-wire path. Range 0 ,
0x77 | 13 | 14 | WaterngStatus | Byte |  |  |  | 1226 | DecMod2 | Watering status. Range is 0 to 1. 0 = Module is not watering. 1 = Module is watering. | 000 | Ai | 1226 | 0x77_DecMod2WaterngStatus , DA_Ai ,1226 ,Ai ,1226 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Watering status. Range is 0 to 1. 0 = M ,
0x77 | 14 | 15 | OverloadStatus | Byte |  |  |  | 1227 | DecMod2 | Overload status. Range is 0 to 1. 0 = Module is not overloaded. 1 = Module is overloaded. | 000 | Ai | 1227 | 0x77_DecMod2OverloadStatus , DA_Ai ,1227 ,Ai ,1227 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Overload status. Range is 0 to 1. 0 = M ,
0x77 | 15 | 16 | A/DFullScale | Byte |  |  |  | 1228 | DecMod2 | A2D is at full scale. Value is only valid if module is overloaded. Range is 0 to 1. 0 = A/D is not full scale. 1 = A/D is full scale. | 000 | Ai | 1228 | 0x77_DecMod2A/DFullScale , DA_Ai ,1228 ,Ai ,1228 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,A2D is at full scale. Value is only val ,
0x77 | 16 | 17 | Ph1/2Mismatch | Byte |  |  |  | 1229 | DecMod2 | Phase 1/2 mismatch. Value is only valid if module is overloaded. Range is 0 to 1. 0 = Phase 1/2 is not mismatched. 1 = Phase 1/2 is mismatched. | 000 | Ai | 1229 | 0x77_DecMod2Ph1/2Mismatch , DA_Ai ,1229 ,Ai ,1229 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Phase 1/2 mismatch. Value is only valid ,
0x77 | 17 | 18 | LockOutTime | UINT16 |  |  |  | 1230 | DecMod2 | Seconds remaining if the Decoder Module has been locked out by the Facepakc due to ongoing overloads. Value is only valid module is overloaded. Valid values are 0 to 3600. | 000 | Ai | 1230 | 0x77_DecMod2LockOutTime , DA_Ai ,1230 ,Ai ,1230 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds remaining if the Decoder Module ,
0x77 | 18 | 19 | DecModNum | Byte |  |  |  | 1231 | DecMod3 | Decoder Module Number reporting information. Range is 1 to 3. | 000 | Ai | 1231 | 0x77_DecMod3DecModNum , DA_Ai ,1231 ,Ai ,1231 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module Number reporting informa ,
0x77 | 19 | 20 | Installed | Byte |  |  |  | 1232 | DecMod3 | Decoder Module is installed. If module is not installed then all remaining bytes for the module will be 0 and should be ignored. Range is 0 to 1. 0 = Not Installed. 1 = Installed. | 000 | Ai | 1232 | 0x77_DecMod3Installed , DA_Ai ,1232 ,Ai ,1232 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Decoder Module is installed. If module ,
0x77 | 20 | 21 | PathStatus | Byte |  |  |  | 1233 | DecMod3 | Status of the 2-wire path. Range is 0 to 1. 0 = 2-wire path is off. 1 = 2-wire path is on. | 000 | Ai | 1233 | 0x77_DecMod3PathStatus , DA_Ai ,1233 ,Ai ,1233 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Status of the 2-wire path. Range is 0 t ,
0x77 | 21 | 22 | OutputMode | Byte |  |  |  | 1234 | DecMod3 | Output mode of the 2-wire path. Range 0 to 1. 0 = Normal output mode. 1 = Wire test mode (60Hz). | 000 | Ai | 1234 | 0x77_DecMod3OutputMode , DA_Ai ,1234 ,Ai ,1234 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Output mode of the 2-wire path. Range 0 ,
0x77 | 22 | 23 | WaterngStatus | Byte |  |  |  | 1235 | DecMod3 | Watering status. Range is 0 to 1. 0 = Module is not watering. 1 = Module is watering. | 000 | Ai | 1235 | 0x77_DecMod3WaterngStatus , DA_Ai ,1235 ,Ai ,1235 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Watering status. Range is 0 to 1. 0 = M ,
0x77 | 23 | 24 | OverloadStatus | Byte |  |  |  | 1236 | DecMod3 | Overload status. Range is 0 to 1. 0 = Module is not overloaded. 1 = Module is overloaded. | 000 | Ai | 1236 | 0x77_DecMod3OverloadStatus , DA_Ai ,1236 ,Ai ,1236 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Overload status. Range is 0 to 1. 0 = M ,
0x77 | 24 | 25 | A/DFullScale | Byte |  |  |  | 1237 | DecMod3 | A2D is at full scale. Value is only valid if module is overloaded. Range is 0 to 1. 0 = A/D is not full scale. 1 = A/D is full scale. | 000 | Ai | 1237 | 0x77_DecMod3A/DFullScale , DA_Ai ,1237 ,Ai ,1237 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,A2D is at full scale. Value is only val ,
0x77 | 25 | 26 | Ph1/2Mismatch | Byte |  |  |  | 1238 | DecMod3 | Phase 1/2 mismatch. Value is only valid if module is overloaded. Range is 0 to 1. 0 = Phase 1/2 is not mismatched. 1 = Phase 1/2 is mismatched. | 000 | Ai | 1238 | 0x77_DecMod3Ph1/2Mismatch , DA_Ai ,1238 ,Ai ,1238 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Phase 1/2 mismatch. Value is only valid ,
0x77 | 26 | 27 | LockOutTime | UINT16 |  |  |  | 1239 | DecMod3 | Seconds remaining if the Decoder Module has been locked out by the Facepakc due to ongoing overloads. Value is only valid module is overloaded. Valid values are 0 to 3600. | 000 | Ai | 1239 | 0x77_DecMod3LockOutTime , DA_Ai ,1239 ,Ai ,1239 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Seconds remaining if the Decoder Module ,
000
0x78 | Reserved for future use | [9 empty] | 000
0x79 | Reserved for future use | [9 empty] | 000
000
000
000
0x7A – REPORT FLOW TOTALS | [10 empty] | 000 |  |  |  |  | 0x7A – REPORT FLOW TOTALS
| demo=h7a-day.html | [9 empty] | 000
| demo=h7a-week.html | [9 empty] | 000
| demo=h7a-moth.html | [9 empty] | 000
| demo=h7a-year.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
000
| This command will report flow total records stored in the Controller’s EEPROM for the requested flow total type starting with the specified record index. There are 31 Day totals, 5 Week totals, 12 Month totals, and 5 Year totals records available to report. Each record contains a total for the Controller and each of the 6 Flow Sensors in the controller. All values are in gallons. Depending on the totals requested, multiple requests of this command may be required to retrieve all the records since only 7 day/week/month or 4 year totals fit in a single transmission. The Record Index is sent in the request for this purpose. Requests should be made until all records have been reported. | [9 empty] | 000
| This request does not carry a payload. The data in the response is extracted and stored as shown below. | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x7A | Uses ACC2_option1 param from config file | 1 | Type | Byte | [5 empty] | Value indicating the type of flow total being requested. Range is 0 to 3. | 000
0x7A | 0 | 2 | Trigger_RecordIndexDay | Byte |  | 382 |  |  |  | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Av | 382 | 0x7A_Trigger_RecordIndexDay , DA_Av ,382 ,Av ,382 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | Store | [9 empty] | 000
0x7A | Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x7A | 2 | 1 | Type | Byte |  |  |  | 1240 | Day | Value indicating the type of flow total being requested. Range is 0 to 3. | 000 | Ai | 1240 | 0x7A_DayType , DA_Ai ,1240 ,Ai ,1240 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the type of flow total ,
0x7A | 3 | 2 | RecordIndex | Byte |  |  |  | 1241 | Day | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Ai | 1241 | 0x7A_DayRecordIndex , DA_Ai ,1241 ,Ai ,1241 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 4 | 3 | Count | Byte |  |  |  | 1242 | Day | Value indicating the number of records being reported. Range is 0 to 7 for Day- Week- and Month flow totals. Range is 0 to 4 for Year totals. | 000 | Ai | 1242 | 0x7A_DayCount , DA_Ai ,1242 ,Ai ,1242 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of records ,
0x7A | 5 | 4 | TimeStamp | 4 Bytes |  |  |  | 1243 | Day | Unix Time Stamp for the reported record. The time stamp is dependent upon the flow total type requested. A value of 0 indicates that the recod is empty and should not be used. | 000 | Ai | 1243 | 0x7A_DayTimeStamp , DA_Ai ,1243 ,Ai ,1243 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unix Time Stamp for the reported record ,
0x7A | 6 | 5 | ConTot | 4 or 8 Bytes |  |  |  | 1244 | Day | Flow Value holding the controller flow total. | 000 | Ai | 1244 | 0x7A_DayConTot , DA_Ai ,1244 ,Ai ,1244 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value holding the controller flow ,
0x7A | 7 | 6 | FlowSensor1 | 4 or 8 Bytes |  |  |  | 1245 | Day | Flow Value for FlowSensor1 | 000 | Ai | 1245 | 0x7A_DayFlowSensor1 , DA_Ai ,1245 ,Ai ,1245 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor1 ,
0x7A | 8 | 7 | FlowSensor2 | 4 or 8 Bytes |  |  |  | 1246 | Day | Flow Value for FlowSensor2 | 000 | Ai | 1246 | 0x7A_DayFlowSensor2 , DA_Ai ,1246 ,Ai ,1246 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor2 ,
0x7A | 9 | 8 | FlowSensor3 | 4 or 8 Bytes |  |  |  | 1247 | Day | Flow Value for FlowSensor3 | 000 | Ai | 1247 | 0x7A_DayFlowSensor3 , DA_Ai ,1247 ,Ai ,1247 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor3 ,
0x7A | 10 | 9 | FlowSensor4 | 4 or 8 Bytes |  |  |  | 1248 | Day | Flow Value for FlowSensor4 | 000 | Ai | 1248 | 0x7A_DayFlowSensor4 , DA_Ai ,1248 ,Ai ,1248 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor4 ,
0x7A | 11 | 10 | FlowSensor5 | 4 or 8 Bytes |  |  |  | 1249 | Day | Flow Value for FlowSensor5 | 000 | Ai | 1249 | 0x7A_DayFlowSensor5 , DA_Ai ,1249 ,Ai ,1249 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor5 ,
0x7A | 12 | 11 | FlowSensor6 | 4 or 8 Bytes |  |  |  | 1250 | Day | Flow Value for FlowSensor6 | 000 | Ai | 1250 | 0x7A_DayFlowSensor6 , DA_Ai ,1250 ,Ai ,1250 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor6 ,
0x7A | [10 empty] | 000
0x7A | 0 | 2 | Trigger_RecordIndexWeek | Byte |  | 383 |  |  |  | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Av | 383 | 0x7A_Trigger_RecordIndexWeek , DA_Av ,383 ,Av ,383 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 2 | 1 | Type | Byte |  |  |  | 1251 | Week | Value indicating the type of flow total being requested. Range is 0 to 3. | 000 | Ai | 1251 | 0x7A_WeekType , DA_Ai ,1251 ,Ai ,1251 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the type of flow total ,
0x7A | 3 | 2 | RecordIndex | Byte |  |  |  | 1252 | Week | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Ai | 1252 | 0x7A_WeekRecordIndex , DA_Ai ,1252 ,Ai ,1252 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 4 | 3 | Count | Byte |  |  |  | 1253 | Week | Value indicating the number of records being reported. Range is 0 to 7 for Day- Week- and Month flow totals. Range is 0 to 4 for Year totals. | 000 | Ai | 1253 | 0x7A_WeekCount , DA_Ai ,1253 ,Ai ,1253 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of records ,
0x7A | 5 | 4 | TimeStamp | 4 Bytes |  |  |  | 1254 | Week | Unix Time Stamp for the reported record. The time stamp is dependent upon the flow total type requested. A value of 0 indicates that the recod is empty and should not be used. | 000 | Ai | 1254 | 0x7A_WeekTimeStamp , DA_Ai ,1254 ,Ai ,1254 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unix Time Stamp for the reported record ,
0x7A | 6 | 5 | ConTot | 4 or 8 Bytes |  |  |  | 1255 | Week | Flow Value holding the controller flow total. | 000 | Ai | 1255 | 0x7A_WeekConTot , DA_Ai ,1255 ,Ai ,1255 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value holding the controller flow ,
0x7A | 7 | 6 | FlowSensor1 | 4 or 8 Bytes |  |  |  | 1256 | Week | Flow Value for FlowSensor1 | 000 | Ai | 1256 | 0x7A_WeekFlowSensor1 , DA_Ai ,1256 ,Ai ,1256 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor1 ,
0x7A | 8 | 7 | FlowSensor2 | 4 or 8 Bytes |  |  |  | 1257 | Week | Flow Value for FlowSensor2 | 000 | Ai | 1257 | 0x7A_WeekFlowSensor2 , DA_Ai ,1257 ,Ai ,1257 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor2 ,
0x7A | 9 | 8 | FlowSensor3 | 4 or 8 Bytes |  |  |  | 1258 | Week | Flow Value for FlowSensor3 | 000 | Ai | 1258 | 0x7A_WeekFlowSensor3 , DA_Ai ,1258 ,Ai ,1258 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor3 ,
0x7A | 10 | 9 | FlowSensor4 | 4 or 8 Bytes |  |  |  | 1259 | Week | Flow Value for FlowSensor4 | 000 | Ai | 1259 | 0x7A_WeekFlowSensor4 , DA_Ai ,1259 ,Ai ,1259 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor4 ,
0x7A | 11 | 10 | FlowSensor5 | 4 or 8 Bytes |  |  |  | 1260 | Week | Flow Value for FlowSensor5 | 000 | Ai | 1260 | 0x7A_WeekFlowSensor5 , DA_Ai ,1260 ,Ai ,1260 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor5 ,
0x7A | 12 | 11 | FlowSensor6 | 4 or 8 Bytes |  |  |  | 1261 | Week | Flow Value for FlowSensor6 | 000 | Ai | 1261 | 0x7A_WeekFlowSensor6 , DA_Ai ,1261 ,Ai ,1261 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor6 ,
0x7A | [10 empty] | 000
0x7A | 0 | 2 | Trigger_RecordIndexMonth | Byte |  | 384 |  |  |  | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Av | 384 | 0x7A_Trigger_RecordIndexMonth , DA_Av ,384 ,Av ,384 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 2 | 1 | Type | Byte |  |  |  | 1262 | Month | Value indicating the type of flow total being requested. Range is 0 to 3. | 000 | Ai | 1262 | 0x7A_MonthType , DA_Ai ,1262 ,Ai ,1262 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the type of flow total ,
0x7A | 3 | 2 | RecordIndex | Byte |  |  |  | 1263 | Month | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Ai | 1263 | 0x7A_MonthRecordIndex , DA_Ai ,1263 ,Ai ,1263 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 4 | 3 | Count | Byte |  |  |  | 1264 | Month | Value indicating the number of records being reported. Range is 0 to 7 for Day- Week- and Month flow totals. Range is 0 to 4 for Year totals. | 000 | Ai | 1264 | 0x7A_MonthCount , DA_Ai ,1264 ,Ai ,1264 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of records ,
0x7A | 5 | 4 | TimeStamp | 4 Bytes |  |  |  | 1265 | Month | Unix Time Stamp for the reported record. The time stamp is dependent upon the flow total type requested. A value of 0 indicates that the recod is empty and should not be used. | 000 | Ai | 1265 | 0x7A_MonthTimeStamp , DA_Ai ,1265 ,Ai ,1265 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unix Time Stamp for the reported record ,
0x7A | 6 | 5 | ConTot | 4 or 8 Bytes |  |  |  | 1266 | Month | Flow Value holding the controller flow total. | 000 | Ai | 1266 | 0x7A_MonthConTot , DA_Ai ,1266 ,Ai ,1266 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value holding the controller flow ,
0x7A | 7 | 6 | FlowSensor1 | 4 or 8 Bytes |  |  |  | 1267 | Month | Flow Value for FlowSensor1 | 000 | Ai | 1267 | 0x7A_MonthFlowSensor1 , DA_Ai ,1267 ,Ai ,1267 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor1 ,
0x7A | 8 | 7 | FlowSensor2 | 4 or 8 Bytes |  |  |  | 1268 | Month | Flow Value for FlowSensor2 | 000 | Ai | 1268 | 0x7A_MonthFlowSensor2 , DA_Ai ,1268 ,Ai ,1268 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor2 ,
0x7A | 9 | 8 | FlowSensor3 | 4 or 8 Bytes |  |  |  | 1269 | Month | Flow Value for FlowSensor3 | 000 | Ai | 1269 | 0x7A_MonthFlowSensor3 , DA_Ai ,1269 ,Ai ,1269 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor3 ,
0x7A | 10 | 9 | FlowSensor4 | 4 or 8 Bytes |  |  |  | 1270 | Month | Flow Value for FlowSensor4 | 000 | Ai | 1270 | 0x7A_MonthFlowSensor4 , DA_Ai ,1270 ,Ai ,1270 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor4 ,
0x7A | 11 | 10 | FlowSensor5 | 4 or 8 Bytes |  |  |  | 1271 | Month | Flow Value for FlowSensor5 | 000 | Ai | 1271 | 0x7A_MonthFlowSensor5 , DA_Ai ,1271 ,Ai ,1271 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor5 ,
0x7A | 12 | 11 | FlowSensor6 | 4 or 8 Bytes |  |  |  | 1272 | Month | Flow Value for FlowSensor6 | 000 | Ai | 1272 | 0x7A_MonthFlowSensor6 , DA_Ai ,1272 ,Ai ,1272 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor6 ,
0x7A | [10 empty] | 000
0x7A | 0 | 2 | Trigger_RecordIndexYear | Byte |  | 385 |  |  |  | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Av | 385 | 0x7A_Trigger_RecordIndexYear , DA_Av ,385 ,Av ,385 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 2 | 1 | Type | Byte |  |  |  | 1273 | Year | Value indicating the type of flow total being requested. Range is 0 to 3. | 000 | Ai | 1273 | 0x7A_YearType , DA_Ai ,1273 ,Ai ,1273 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the type of flow total ,
0x7A | 3 | 2 | RecordIndex | Byte |  |  |  | 1274 | Year | Value indicating the starting record infex to use when reporting totals. Ranges are dependent upon the flow total type requested. | 000 | Ai | 1274 | 0x7A_YearRecordIndex , DA_Ai ,1274 ,Ai ,1274 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the starting record in ,
0x7A | 4 | 3 | Count | Byte |  |  |  | 1275 | Year | Value indicating the number of records being reported. Range is 0 to 7 for Day- Week- and Month flow totals. Range is 0 to 4 for Year totals. | 000 | Ai | 1275 | 0x7A_YearCount , DA_Ai ,1275 ,Ai ,1275 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the number of records ,
0x7A | 5 | 4 | TimeStamp | 4 Bytes |  |  |  | 1276 | Year | Unix Time Stamp for the reported record. The time stamp is dependent upon the flow total type requested. A value of 0 indicates that the recod is empty and should not be used. | 000 | Ai | 1276 | 0x7A_YearTimeStamp , DA_Ai ,1276 ,Ai ,1276 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Unix Time Stamp for the reported record ,
0x7A | 6 | 5 | ConTot | 4 or 8 Bytes |  |  |  | 1277 | Year | Flow Value holding the controller flow total. | 000 | Ai | 1277 | 0x7A_YearConTot , DA_Ai ,1277 ,Ai ,1277 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value holding the controller flow ,
0x7A | 7 | 6 | FlowSensor1 | 4 or 8 Bytes |  |  |  | 1278 | Year | Flow Value for FlowSensor1 | 000 | Ai | 1278 | 0x7A_YearFlowSensor1 , DA_Ai ,1278 ,Ai ,1278 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor1 ,
0x7A | 8 | 7 | FlowSensor2 | 4 or 8 Bytes |  |  |  | 1279 | Year | Flow Value for FlowSensor2 | 000 | Ai | 1279 | 0x7A_YearFlowSensor2 , DA_Ai ,1279 ,Ai ,1279 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor2 ,
0x7A | 9 | 8 | FlowSensor3 | 4 or 8 Bytes |  |  |  | 1280 | Year | Flow Value for FlowSensor3 | 000 | Ai | 1280 | 0x7A_YearFlowSensor3 , DA_Ai ,1280 ,Ai ,1280 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor3 ,
0x7A | 10 | 9 | FlowSensor4 | 4 or 8 Bytes |  |  |  | 1281 | Year | Flow Value for FlowSensor4 | 000 | Ai | 1281 | 0x7A_YearFlowSensor4 , DA_Ai ,1281 ,Ai ,1281 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor4 ,
0x7A | 11 | 10 | FlowSensor5 | 4 or 8 Bytes |  |  |  | 1282 | Year | Flow Value for FlowSensor5 | 000 | Ai | 1282 | 0x7A_YearFlowSensor5 , DA_Ai ,1282 ,Ai ,1282 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor5 ,
0x7A | 12 | 11 | FlowSensor6 | 4 or 8 Bytes |  |  |  | 1283 | Year | Flow Value for FlowSensor6 | 000 | Ai | 1283 | 0x7A_YearFlowSensor6 , DA_Ai ,1283 ,Ai ,1283 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Flow Value for FlowSensor6 ,
000
0x7B – REPORT FLOW DETAIL DATA | [10 empty] | 000 |  |  |  |  | 0x7B – REPORT FLOW DETAIL DATA
| Not Implemented | [9 empty] | 000
| This command will report detailed flow rate data that is stored in the facepack’s EEPROM for each of the 6 flow sensors. The Facepack can store flow detail data points at five-minute intervals for up to 7 days. All flow values returned are in GPM. Depending on the number of records that need to be retrieved, multiple requests of this command may be required to retrieve all the records since only 20 of the 2016 records fit in a single transmission. Requests should be made until the current time of day has been reached. | [9 empty] | 000
| This request does not carry a payload. The data in the response is extracted and stored as shown below. | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x7B | 0 | 1 | TimeStamp | UINT32 | [5 empty] | Unix Time Stamp of the date/time for which to report the stored flow detail data. The time stamp should be on a 5-minute interval with no seconds. Time stamps not on this 5-minute interval will be foreced to the 5-minute interval just prior to the value sent. | 000
0x7B | 1 | 2 | Count | Byte | [5 empty] | Number of flow detail data records being reported. Range is 1 to 20. | 000
0x7B | 2 | 3 | FlowSen1Detail | UINT16 | [5 empty] | Part of FlowDetailRecordX. Range of FlowDetailRecord is 0 to 19. Flow rate data point for each of the 6 Flow Sensors in the Controller. Values are in GPM. Range is 1 to 10-000. | 000
0x7B | 3 | 4 | FlowSen2Detail | UINT16 | [5 empty] | Part of FlowDetailRecordX. Range of FlowDetailRecord is 0 to 19. Flow rate data point for each of the 6 Flow Sensors in the Controller. Values are in GPM. Range is 1 to 10-000. | 000
0x7B | 4 | 5 | FlowSen3Detail | UINT16 | [5 empty] | Part of FlowDetailRecordX. Range of FlowDetailRecord is 0 to 19. Flow rate data point for each of the 6 Flow Sensors in the Controller. Values are in GPM. Range is 1 to 10-000. | 000
0x7B | 5 | 6 | FlowSen4Detail | UINT16 | [5 empty] | Part of FlowDetailRecordX. Range of FlowDetailRecord is 0 to 19. Flow rate data point for each of the 6 Flow Sensors in the Controller. Values are in GPM. Range is 1 to 10-000. | 000
0x7B | 6 | 7 | FlowSen5Detail | UINT16 | [5 empty] | Part of FlowDetailRecordX. Range of FlowDetailRecord is 0 to 19. Flow rate data point for each of the 6 Flow Sensors in the Controller. Values are in GPM. Range is 1 to 10-000. | 000
0x7B | 7 | 8 | FlowSen6Detail | UINT16 | [5 empty] | Part of FlowDetailRecordX. Range of FlowDetailRecord is 0 to 19. Flow rate data point for each of the 6 Flow Sensors in the Controller. Values are in GPM. Range is 1 to 10-000. | 000
000
000
0x7C - Clear Flow Alarms | [10 empty] | 000 |  |  |  |  | 0x7C - Clear Flow Alarms
| demo=h7c.html | [9 empty] | 000
| Template=Type3 | [9 empty] | 000
000
| This command will allow active flow alarms to be manually cleared. | [9 empty] | 000
000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x7C | 0 | 1 | Trigger_ClearFlowAlarms |  | 36 |  |  |  |  | Write to this point to trigger the action. Value is not important | 000 | Bv | 36 | 0x7C_Trigger_ClearFlowAlarms , DA_Bv ,036 ,Bv ,036 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Write to this point to trigger the acti ,
0x7C | 1 | 2 | Ws1Alarm | Byte |  | 386 |  |  |  | Value indicating whether or not to clear a specific MainSafe alarm. These bytes are ignored if all MainSafe Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 386 | 0x7C_Ws1Alarm , DA_Av ,386 ,Av ,386 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 2 | 3 | Ws2Alarm | Byte |  | 387 |  |  |  | Value indicating whether or not to clear a specific MainSafe alarm. These bytes are ignored if all MainSafe Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 387 | 0x7C_Ws2Alarm , DA_Av ,387 ,Av ,387 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 3 | 4 | Ws3Alarm | Byte |  | 388 |  |  |  | Value indicating whether or not to clear a specific MainSafe alarm. These bytes are ignored if all MainSafe Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 388 | 0x7C_Ws3Alarm , DA_Av ,388 ,Av ,388 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 4 | 5 | Ws4Alarm | Byte |  | 389 |  |  |  | Value indicating whether or not to clear a specific MainSafe alarm. These bytes are ignored if all MainSafe Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 389 | 0x7C_Ws4Alarm , DA_Av ,389 ,Av ,389 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 5 | 6 | Ws5Alarm | Byte |  | 390 |  |  |  | Value indicating whether or not to clear a specific MainSafe alarm. These bytes are ignored if all MainSafe Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 390 | 0x7C_Ws5Alarm , DA_Av ,390 ,Av ,390 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 6 | 7 | Ws5Alarm | Byte |  | 391 |  |  |  | Value indicating whether or not to clear a specific MainSafe alarm. These bytes are ignored if all MainSafe Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 391 | 0x7C_Ws5Alarm , DA_Av ,391 ,Av ,391 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 7 | 8 | Fz1Alarm | Byte |  | 392 |  |  |  | Value indicating whether or not to clear a specific Flow Zone alarm. These bytes are ignored if all Flow Zone Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 392 | 0x7C_Fz1Alarm , DA_Av ,392 ,Av ,392 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 8 | 9 | Fz2Alarm | Byte |  | 393 |  |  |  | Value indicating whether or not to clear a specific Flow Zone alarm. These bytes are ignored if all Flow Zone Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 393 | 0x7C_Fz2Alarm , DA_Av ,393 ,Av ,393 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 9 | 10 | Fz3Alarm | Byte |  | 394 |  |  |  | Value indicating whether or not to clear a specific Flow Zone alarm. These bytes are ignored if all Flow Zone Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 394 | 0x7C_Fz3Alarm , DA_Av ,394 ,Av ,394 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 10 | 11 | Fz4Alarm | Byte |  | 395 |  |  |  | Value indicating whether or not to clear a specific Flow Zone alarm. These bytes are ignored if all Flow Zone Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 395 | 0x7C_Fz4Alarm , DA_Av ,395 ,Av ,395 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 11 | 12 | Fz5Alarm | Byte |  | 396 |  |  |  | Value indicating whether or not to clear a specific Flow Zone alarm. These bytes are ignored if all Flow Zone Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 396 | 0x7C_Fz5Alarm , DA_Av ,396 ,Av ,396 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
0x7C | 12 | 13 | Fz6Alarm | Byte |  | 397 |  |  |  | Value indicating whether or not to clear a specific Flow Zone alarm. These bytes are ignored if all Flow Zone Alarms are being cleared. Range is 0 to 1. 0 = Do not clear all alarm 1 = Clear alarm | 000 | Av | 397 | 0x7C_Fz6Alarm , DA_Av ,397 ,Av ,397 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating whether or not to clea ,
000
0x7D - 0x99 - Services Not implemented
000
000
0x9A – GET CONTROLLER VERSION TYPE (v2.11.006 and later) | [10 empty] | 000 |  |  |  |  | 0x9A – GET CONTROLLER VERSION TYPE (v2.11.006 and later)
| demo=h9a.html | [9 empty] | 000
| Template=Type2 | [9 empty] | 000
000
| This command is used to determine the Controller model and the current firmware version. It can be used by the central to determine Controller models in mixed systems where different Controller models are connected to the same communications network. A System ID of 00H (All Controllers) or 85H (ACC2 Controllers) may be used with this command. | [9 empty] | 000
| This request does not carry a payload. The data in the response is extracted and stored as shown below. | [9 empty] | 000
| Store | [9 empty] | 000
| Offset | item | Variable/ Data | Data Type | [5 empty] | Description | 000
0x9A | 0 | 1 | FwVers | UINT16 |  |  |  | 1284 |  | Integer value of firmware version times 100. | 000 | Ai | 1284 | 0x9A_FwVers , DA_Ai ,1284 ,Ai ,1284 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Integer value of firmware version times ,
0x9A | 1 | 2 | EngRev | Byte |  |  |  | 1285 |  | Integer value of firmware Engineering Revision. Range is 0 to 255. | 000 | Ai | 1285 | 0x9A_EngRev , DA_Ai ,1285 ,Ai ,1285 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Integer value of firmware Engineering R ,
0x9A | 2 | 3 | Model | Byte |  |  |  | 1286 |  | Value indicating Controller Model. Always returns a fixed value of 42 (ACC2 Controller). | 000 | Ai | 1286 | 0x9A_Model , DA_Ai ,1286 ,Ai ,1286 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating Controller Model. Alwa ,
0x9A | 3 | 4 | Type | Byte |  |  |  | 1287 |  | Value indicating the Controller Type. Range is 0 to 2. | 000 | Ai | 1287 | 0x9A_Type , DA_Ai ,1287 ,Ai ,1287 , Server ,vHunterAcc2 , Present_value , No_Units ,0 , 100, 0, 100,Value indicating the Controller Type. R ,
000
000
000
000
000
000
000
000
000
000

## Supported Services
Striketrough = Not Supported
If the services is not in this list then it is not supported
Services supported for ACC2 firmware as shipped by Hunter in Jan2020
Services to support older ACC2 firmware - May be available on Request
Hunter_CMD / Services Supported
0x01 – SET FIELD CONTROLLER SYSTEM GLOBALS
0x02 – REPORT FIELD CONTROLLER GLOBALS
0x03 – SET STACKING MODE AND LIMITS
0x04 – REPORT STACKING MODE AND LIMITS
0x06 – Mute
0x07 - Reset Mute
0x0A – REPORT VERSIONS
0x0C – SET FLOW OPERATION PARAMETERS
0x0D – REPORT FLOW OPERATION PARAMETERS
0x0E – REPORT ITEM INFORMATION
0x10 – SET DECODER MODULE STATION ASSIGNMENTS (v2.00.016 and later)
0x12 – SET ITEM NAMES (v2.00.016 and later)
0x13 – SET STATION PARAMETERS
0x15 – REPORT DECODER MODULE STATION ASSIGNMENTS (v2.00.016 and later)
0x16 - Set Pump / Master Valve Param
0x17 – SET MAINSAFE PARAMETERS
0x18 – REPORT MAINSAFE PARAMETERS
0x19 – SET FLOW ZONE PARAMETERS
0x1A – REPORT FLOW ZONE PARAMETERS
0x1B – SET FLO+A694W SENSOR PARAMETERS (v2.00.033 and later)
0x1c– SET CLICK SENSOR PARAMS
0x1D – SET PROGRAM SENSOR ACTION
0x1E – SET FIELD CONTROLLER PROGRAM HEADER DATA (v2.13.000 and Later)
0x1F – SET FIELD CONTROLLER PROGRAM EVENT RUN TIME DATA
0x20 – SET RAIN DELAY VALUES
0x21 – GET RAIN DELAY VALUES
0x23 – SET SEASONAL ADJUST VALUES
0x24 – STOP STATIONS
0x25 – REPORT SEASONAL ADJUST VALUES
0x26 – STOP A PROGRAM
0x27 – DECODER INVENTORY
0x28 – PURGE LOG RECORDS
0x2B – REPORT FLOW ZONE MONITORING DATA
0x2C – REPORT FLOW ZONE DIAGNOSTIC DATA
0x2D – REPORT MAINSAFE MONITORING DATA
0x2E – REPORT FLOW MANAGEMENT FLOW DATA
0x2F – REPORT FLOW MANAGEMENT ACTIVE STATION DATA
0x30 – REPORT CONTROLLER CURRENT DRAWS (v2.00.016 and later)
0x32 – REPORT ITEM NAMES (v.2.00.016 and later)
0x33 – REPORT STATION PARAMETERS (v.2.00.016 and later)
0x34 – Report Block Parameters
0x35 – Stop Blocks
0x36 – REPORT PUMP/MASTER VALVE PARAMETERS (v2.11.007 and later)
0x37 – Reserved for Future
0x38 – SET LEARN FLOW START/STOP TIME
0x39 – GET LEARN FLOW STATUS INFO
0x3A – Get Learn Flow Report Info
0x3B – REPORT FLOW SENSOR PARAMETERS (v2.00.033 and Later)
0x3C – REPORT CLICK SENSOR PARAMETERS
0x3D – REPORT PROGRAM SENSOR ACTION
0x3E – REPORT FIELD CONTROLLER PROGRAM HEADER DATA (v2.13.000 and Later)
0x3F – Report Field Controller Program Event Run Time Data
0x40 - Set User Management Information
0x41 - Report User Management Information
0x42 – Set Calendar Days Off
0x43 – Get Calendar Days Off
0x4f - Report Item CRCs
0x51 – Stop Irrigation
0x51 – Stop Irrigation
0x52 – Programmable Off
0x53 – Suspend Irrigation
0x54 – Cancel Programmable Off
0x55 – Cancel Suspend
0x56 – Start Manual All Station Program
0x57 – Set System Event Mode
0x58 – Set FCP Mode
0x59 – Clear Field Controller Display Messages
0x5A – Set Pause Mode
0x5B – Cancel Pause Mode
0x5C – Start Single Manual Event
0x5D – Start Multiple Manual Events
0x5e - 0x71
0x72 – REPORT ACTIVE OUTPUTS (v2.00.025)
0x73 – REPORT ALARMS/INFORMATION
0x74 – REPORT LOG
0x75 – REPORT CURRENT FLOW DATA
0x76 – REPORT CLIK SENSOR INFORMATION
0x77 – REPORT DECODER MODULE INFORMATION (v2.00.024 and later)
0x7A – REPORT FLOW TOTALS
0x7B – REPORT FLOW DETAIL DATA
0x7C - Clear Flow Alarms
0x9A – GET CONTROLLER VERSION TYPE (v2.11.006 and later)

## Revisions
Rev 2 | 2020Jan03 | Record which web pages are used for each service
Fixed Column Y which had some #ref
Fixed some rows in the bacnet objects column